## Source-Specific Q&A
Date | Who's Asking? | Entity | Subject or Subpart | Contact name | Contact info | Question or Issue Description | Answer or Follow-up
2012-04-26 | Farabee Mechanical | Distributor | NESHAP 4Z | Donna Oehm | > Donna Oehm, CSM > Farabee Mechanical, Inc. > PO Box 1748 > Hickman, NE 68372 > farabeecsm@inebraska.com > 402.792.2612 office > 402.405.7288 cell | Question: Once we install catalytic converters and submit the performance > test that shows it meets the CO reduction requirement at Benkelman, NE, can > they take the elements out until May 3rd, 2013 (or May 2nd just in case they > run at midnight)? > > > > Is there anything wrong with that? They'd like to keep the element clean > until they absolutely have to put it in. The CO reduction would be the same as listed on the performance test results > once they re-installed the elements in May 2013, it is just if they ran between > now and then, the CO output would be back to pre-catalyst measures. I didn't > see a problem with it, but need reassurance. | Donna, I agree with Eric & Melissa that usually a retest is not required for the removal and re-installation of a catalyst. A retest could be required, however, if the initial test is no longer representative of the performance of the affected source. I wouldn't think that the removal and re-installation of the catalytic converter elements would cause the initial test to no longer be representative. The other issue is not as apparent to me. I believe your question is - once a facility installs a catalytic converter system and demonstrates compliance with the RICE MACT emission limits through a stack test, can the owner remove the catalytic converter elements, operate the engine without the catalytic converter elements (and likely have emissions over the RICE MACT limits), and then reinstall the catalytic converter elements prior to the initial compliance date. I don't immediately see a problem with that either but I am not sure how the subsequent testing provisions would apply in that case. For example, in certain cases a subsequent test is required every 8,760 hours of operation of the engine or 3 years from the initial stack test, whichever occurs first. I am not sure which date (e.g., the initial stack test, the initial compliance date) would start the clock on the retest. I will have to get back with you on these issues. Let me know if I am not understanding your question correctly. David Peter Environmental Engineer U.S. EPA Region 7 901 North 5th Street Kansas City, KS 66101 913-551-7397
2012-03-21 | Farabee Mechanical | Distributor | NESHAP 4Z | Donna Oehm | > Donna Oehm, CSM > Farabee Mechanical, Inc. > PO Box 1748 > Hickman, NE 68372 > farabeecsm@inebraska.com > 402.792.2612 office > 402.405.7288 cell | I need to get my head wrapped around is the proposed 60 hours of emergency demand response. Here's what I think I know: * EDM is unplanned, and imminent blackout, with 15 hours currently built into the rule, proposed to be amended to 60 hours. What I don't know is how either the 15 hours or the 60 will allow a municipality to "generate revenue." In all cases, the audience I will be talking to has "capacity credits" to some degree. Is it true that if they have capacity credits, they cannot declare the engines as "emergency" use only? Or am I way off base here? I just need your take on what kind of revenue generation an emergency-use stationary engine can obtain, then I think I would be able to answer most of the proposed questions. | Under the current regulations, I believe that the facility could have a financial arrangement if the power supplied as part of this financial arrangement qualifies as emergency demand response. The following is from the last sentence in 40 CFR 63.6640(f)(1)(iii): The supply of emergency power to another entity or entities pursuant to financial arrangement is not limited by this paragraph (f)(1)(iii), as long as the power provided by the financial arrangement is limited to emergency power. As you are aware, EPA is scheduled to propose changes to the RICE MACT in April. This issue may be addressed in this proposed rulemaking. David Peter Donna: You got it. For subsequent testing, I went with the first occurrence and have informed them that they must send 60-day notice and have the test date prior to April 24th, 2015, which is 3 years from the initial performance test. If we went with 3 years from May 3, 2013, the testing companies would be booked solid in 2016. Benkelman does not anticipate attaining anywhere near 8760 hours of run time…. probably in the engine's lifetime, unless something drastic changes. David: I don't believe that there would be a need to retest once the catalytic converter elements are re-installed.
2012-02-21 | Farabee Mechanical | Distributor | NESHAP 4Z | Donna Oehm | > Donna Oehm, CSM > Farabee Mechanical, Inc. > PO Box 1748 > Hickman, NE 68372 > farabeecsm@inebraska.com > 402.792.2612 office > 402.405.7288 cell | > According to the rule, 63.6640 (b) a new performance test is required if the stationary engine owner changes the catalyst. What about "cleaning" the catalyst? Does this prompt a new test? | Yes, 63.6640(b) states that if the catalyst is changed, you'll need to retest and establish new operating parameters by conducting another initial performance test. Cleaning wouldn't require you to retest.
2012-02-21 | NMC Power | Distributor | NESHAP 4Z | Patrick Henry | pathenry@nmcpower.com | We have a waste water pump station that uses electric pumps to move waste water, in the event that the electric pumps can’t keep up or loss of utility power a diesel engine/pump takes over, when the level lowers back down or utility is restored they go back to their electric pump system. Would this be an emergency engine? They don’t contract with this engine, and they don’t run it at the same time as there electric pumps. The only time it runs is when the demand is too great or loss of utility power. It is greater than 500HP And runs on diesel fuel only | I conferred with EPA Region VII on this and we both agree on the following. The using the engine when power is lost by the local utility would make it an emergency engine. The other situation doesn't appear to qualify as emergency. The pumping of wastewater appears to be part of normal operations. It appears the operation of the backup engine would be avoided if the regular electric engine was larger. The RICE MACT response to comments has a few examples of emergency situations: when electric power from the local utility is interrupted, to pump water in the case of fire or flood, and when a hurricane shutdowns offshore wells. This situation doesn't appear to be similar. The backup engine may qualify as a "limited use" engine if it is used less than 100 hours. Without any additional information, I would say that this engine does not qualify as "emergency" when used for removing excess wastewater and would therefore not be classified as emergency if it is used for both purposes.
2012-01-23 | GTE Exhaust | Distributor | NESHAP 4Z | Andrew Boellstorff | Andrew Boellstorff Manager, Human Capital Development 4121 N.W. 37th Lincoln,NE 68524 Tel: 402-323-7279 Fax: 402-939-0700 web: www.gtexhaust.com aboellstorff@gtexhaust.com | From my understanding of the requirement, just catalyst inlet temperature needs to be reported – there is no requirement for outlet temp. after the catalyst. Is this correct? Again, reading the requirement, it asks that the pressure drop be monitored monthly vs. continuous monitoring of the temperature. Is the EPA looking for the single highest pressure drop measurement at 100% load during a one month period of runs? For the reporting information on the data: Does the EPA or DEQ have some sort of electronic submission database that the operators could upload to or will it be expected that they return printouts of the information along with the Notification of Compliance Status Report? I’m wondering about what kind of format will be the easiest for both the regulator to receive and the operator to print out. With the initial and subsequent performance reports, is there a requirement to document the instrumentation calibration for the O2 and CO monitors? | They only need to record the catalyst inlet temperature and maintain it between >450F and 1350F. The pressure drop of the catalyst needs to be monitored monthly. It should be monitored according to the site-specific monitoring plan developed by each facility. There is no requirement as to when it should be conducted, only that it doesn’t change by more than 2 inches of water at 100 percent load plus or minus 10% from what was measured during the performance test. The rule doesn’t not require sources to report all of their monitoring data, but they do need to keep record of all of their monitoring data. They are required to report their performance test data in the Notification of Compliance Status (on our website) and send reports after each time they conduct a stack test. Their semiannual compliance reports (or annual, if they are limited use engines) only need to include deviations from their requirements. I’m not sure if I understand your last question. The stack testing company will have requirements to follow the methods properly and demonstrate they did so properly, which most likely includes calibrations of the instrumentation. Can you clarify your question?
2011-10-19 | Ashgrove | Source | NESHAP 3L | Melissa Ellis |  | Ashgrove would like to request an extension of their compliance date for the PM & HCl limits in rule due to a settlement negotiation that is ongoing. They want to see what their consent decree will require before they can assess what additional controls they may need to reduce PM & HCl to meet the NESHAP limits. | Even though we are delegated the rule, the EPA withholds some aspects of the rule and rule alternatives for their delegation. 63.1358(c) states the delegated authority cannot approve alternate compliance under 63.1351 - compliance dates
2011-10-19 | Terracon | Consultant | NESHAP 6X | Melissa Ellis |  | Their client has mutliple pieces of equipment all conducting machining. In the NOCS, Section 3, do they have to list each specific unit. | No, if they ae all under the same control device or managed the same under the management practices, they can be grouped according to process line.
2011-09-27 | City of Franklin | Source | NESHAP 4Z | Melissa Ellis |  | Will the president overruling the EPA have any effect on the RICE/NESHAP rules that are to be implemented? My council was just getting convinced to do it but are hoping this will mean that we won't have to. We're having trouble coming up with 200,000 dollars to make the changes to our plant. | We have no indication from EPA or otherwise that the RICE NESHAP will be vacated/overruled. The only changes we foresee related to the RICE NESHAP relates to the reconsideration of how many hours an emergency engine can operate as part of demand response from the regional transmission organization (right now it is 15 hours/year & EPA may increase this).
2011-08-19 | Norther Natural Gas | Source | NESHAP 5D | Greg Ammon | gregory.ammon@nngco.com | One question brought up was regarding initial notifications for boilers and if they still needed to be submitted in September if with the stay of effectiveness in place. I was informed that you stated that they did not need to be submitted under the stay of effectiveness. Did you receive guidance from EPA on this or was this an internal decision within the NDEQ? The only reason that I ask is to cover my facilities located in other states in the region. when EPA lifts the stay is there any chance that the initial notifications will still be tied to the original posting in the Federal Register and still be due on September 17. | If an entire rule is stayed, then nothing in the rule is effective at all, even the notification requirements. If EPA would have partially stayed the rule (for example, only stayed the effectiveness of the emission standards), then it may mean that notifications would still be due. Since the entire rule is stayed, nothing is in effect or due. It is as if it doesn't exist at all. This should be consistent across the nation, but if you'd like to check with other states, feel free. I don't think so because the notice says they won't lift the stay until they have finalized their reconsideration of the rule. They intent to propose the rule changes this October and finalize them next April.
2011-08-05 | Nebraska Machinery | Distributor | NESHAP 4z | Patrick Henry | pathenry@nmcpower.com | I had a question on the RICE NESHAP engines less then 300 HP. in talking with a customer yesterday how low of HP do we need to keep maintenance records? they have some small Honda engines and small light towers these would be comparable to a push lawn mower so they don't have a hour meter and would be around 10-15 HP. They do plan on keeping records on there 50 HP ----300 HP. | Maintenance records need to be kept for all sources subject to the requirements in 4Z.
2011-07-15 | Behlen Mfg. | Source | NESHAP 6X | Don Green | don.green@behlenmfg.com | Where do I take visible emissions readings if we have 4-5 welding areas and 100 openings (vents/doors)? | 63.11516(f)(3) states "You must perform visual determinations of welding fugitive emissions in accordance with……. at the primary vent, stack, exit, or opening…" I spoke with Joe Terriquez from EPA Region VII to clarify what "primary" means. He advised to use the largest vent/opening in a welding area or a vent with a fan drawing the air out of the building. He said it would be sufficient to use one emissions point per welding area and to choose the vent/opening that is apt to have the most emissions drawn through them. He also advised to write this in a procedure, so that you can have consistent readings and justification as to why those vents/openings were chosen.
2011-07-07 | Magellan Pipeline | Source | NESHAP 6B | Brad P. |  | I looked more into the Magellan pipeline 6B test. It is really screwy because they have a flare and they claim they meet the 80mg/l of gasoline reduction because of manufacture specs of the flare as long as they meet the requirement in 60.18 for flares. That is why did method 22 (VE). So the only thing they did that 6B requires is method 21 LDAR. | 63.11092(a)(4) States that the performance test requirements do not apply to flares meeting the requirements in 63.11(b) (see below). They need to demonstrate compliance with 63.11(b) and 60.503(a), (b), and (d). So, I think they did follow the correct compliance demonstration (from what I remember you showing me).
2011-04-14 | Nebraska Machinery | Distributor | NESHAP 4Z | Tracy Henke | 402-891-7656 tracyhenke@nmcpower.com | I have a question that may fall under NSPS rules, however it also has to do with RICE NESHAP. Here is what I have. Can you help give me some guidance? I have a municipality (area source) that is wanting to install and existing (used) CI engine for non-emergency use. This engine is rated at 762 HP (brake horsepower), so greater than 500HP. Here is where it gets interesting. This unit was manufactured (build date) of 8-25-2006. I believe due to the build date that this unit does not fall under NESHAP regulations, correct? This should fall under NSPS regulations for the model year of production, which this unit should already meet, correct? I have included as much information as I could find on the units (EPA Certificate, CARB Certificate). And on pages 4 and 5 of the performance data, there is also emissions data. If this customer is wanting to install this unit as a non-emergency use, I believe we do not have to add aftertreatment, correct? | O.K. I received an answer from EPA Region VII. The first time the engine would have been used at a facility, it would have been considered new because it was constructed after 6/12/06. It would have to comply with the NSPS. Even though it has been moved, it is still considered new under the NESHAP and the requirement is the same to meet the NSPS. The language regarding moving an existing engine confused the issue, but it doesn't apply in this case.
2011-03-29 | Nucor | Source | NESHAP 4Z | Lauren Tietgen | ltietgen@gmail.com | For the RICE regulations, if someone is choosing to use the emergency use only exemption, there is a hour rule (this is from memory, so won't be exact wording from regs): Emergency use - as much as needed No more than 100 hours - maintenance checks and other ...(maintenance checks no more than 50 hours) Has there been any discussion as to whether a facility can self-impose a 50 hour limit on themselves for non-emergency use, so as not to separately document maintenance checks and other? | You would still have to separately document your hours of use even if you had a self-imposed limit in a permit. The rule requires you to keep track of your operating hours and document the use (emergency, required testing, etc.) 63.6655(f). If you can demonstrate that your emergency engine meets the non-emergency emission standards, you wouldn't have to keep documentation of the hours. But, most likely, you wouldn't demonstrate compliance with the non-emergency standards.
2011-01-04 | Offut AFB | Source | NESHAP 6B & 6C | John Parr | john.parr@offutt.af.mil | The air toxics notebook for BBBBBB, says that "Gas Dispensing Facilities", such as retail gas stations, that are subject to CCCCCC, are not subject to BBBBBB. o What is the definition of Gas Dispensing Facility? I could not find it in the regulations. I'm wondering if two of our tanks that I submitted for BBBBBB might be exempt (they are currently submitted for both BBBBBB and CCCCCC). • The air toxics notebook for BBBBBB also states that there is no need for "initial notification" or "compliance status notification" if the tanks comply with NE State Fire Marshal laws for submerged fill o I looked through the NE Fire Marshal Regs and I could not find a straight forward regulation addressing "submerged fill" requirements for ASTs or USTs. Do you by chance have this available? | Hi, John! The Notebook language should be clarified. I hadn't realized it said that. The 12/15/09 proposal clarified this and states "gasoline storage tanks located at bulk facilities, but used only for dispensing gasoline in a manner consistent with tanks located at a gasoline dispensing facility (GDF) as defined at § 63.11132, are not subject to any of the requirements in 40 CFR part 63, subpart BBBBBB. Instead, these tanks must comply with the applicable requirements of 40 CFR part 63, subpart CCCCCC." 63.11132 (within Subpart CCCCCC) states a GDF is "any stationary facility which dispenses gasoline into the fuel tank of a motor vehicle." The point being those tanks you are using to store gasoline that will be put into a vehicle, would only have to comply with 6C & not both 6C & 6B. Does that make more sense? We have found the State Fire Marshall rules & they do require submerged fill. Nebraska Title 159, Chapter 7, 004.01D states all USTs must have submerged fill no more than 6 inches from the bottom of the tank. All GDFs with throughput greater than 10,000 and less than 100,000 gallons are already meeting that requirement under an applicable state regulation - thus, no initial notification or notification of compliance needed for those facilities if they were already operating prior to January 10, 2008. Does this help? Many of those that didn't need to submit a notification did, so it isn't a big deal. You are subject to the rule regardless, you just may not have had to fulfill that requirement.
2010-11-22 | Nebraska Petroleum Marketers | Distributor | NESHAP 6C | Tim Keigher | tkeigher@npcainc.com | Are Petroleum bulk plants and gas stations required to submit a Notification of Compliance Status by January 10, 2011, if we submitted the Initial Notification in 2008? Can't quite figure out the ruling. | Some of the facilities will not have to send in a compliance status notification. Others will be required to submit the compliance status notification by 1/10/11 if they did not certify to compliance in the initial notification. Who has to send in the notifications is on the Air Toxics Notebook, but generally bulk plants <20,000 gallon/day do not have to submit and gas stations <100,000 gallon monthly throughput do not have to submit.
2010-11-15 | SATA | Distributor | NESHAP 6H | David Voth | David Voth Inc. Complete Sales and Marketing 15675 Taylor Street Omaha Nebraska 68116 Phone 402.980.1595 Fax 402.496.8993 davidkvoth@cox.net | Body Shops and some other companies have a spray-on bed liners systems. Companies like Rino Bed Liners and Line-ex bed liners. Check this web site out and let me know. http://www.rhinolinings.com/dealer_info/spray_equipment Do there spray guns have to be HVLP or Compliant? Also. There is a company called Preval Sprayers. This a aerosol type cartridge that is affixed on top of a glass jar of paint. When the cartridge nozzle is pushed down, it sucks up the paint in the jar and sprayed out. Is that system under the aerosol exemption? http://www.preval.com/what-is-preval?ctt_id=8455837&ctt_adnw=Google&ctt_ch=ps&ctt_entity=tc&ctt_cli=2x15169x74271x1755724&ctt_kw=preval%20system&ctt_adid=5772404118&ctt_nwtype=search&gclid=CPrKy-_vmaUCFQFoKgodrxjKIQ | Those spraying bed liners are subject to the regulations and must comply with all aspects of the NESHAP. Only non-refillable aerosol containers are exempt. It sounds as if those you are describing are refillable and do not comply with the rule unless they are 3 oz. or less cup capacities.
2010-11-09 | ADM | Source | NESHAP 4Z | Bob Bauer | robert.bauer@adm.com (402) 562-5081 | It is possible we may want to install a new emergency generator associated with our Dry Mill DDGS Dryers (basically to provide power for operating the feed conveyors during an emergency shutdown condition so that the equipment doesn’t get clogged with feed and can be shut down in an orderly manner). I diligently looked through the presentation on engines that you provided at the last Air Update, and I also attempted to sort through NESHAP Subpart ZZZZ and NSPS Subpart IIII regulations, and I still remain uncertain of the requirements. I’m requesting that you please provide me some guidance on this. Below is further information on what we are proposing: 1) Our facility is an existing major source for HAPs. 2) Although the proposed generator will be installed in the Dry Mill area, I would consider this to be a small stand-alone project separate from the Dry Mill. 3) The diesel generator in question will truly be used for emergency purposes only, will be stationary, and will be rated at approximately 2,013 HP (1,500kW). 4) The unit is currently in the design discussion phase only, but I am assuming it will be a model manufactured in 2010/2011, and will by physically installed sometime in 2011. 5) I have run the maximum PTE calculations (attached), and it does not appear that this unit will trigger any PSD permitting thresholds provided the operating hours are limited by permit to 500 hours per year or less. 6) We would have no problems taking permit restrictions for annual operating hours (unit to be equipped with non-resettable hour meter), and use of only low sulfur diesel fuel (sulfur content not to exceed 0.05%). Can you please let me know whether construction permitting/modeling is necessary to install this unit. Can you also point me in the right direction as to what notifications, testing and recordkeeping would potentially be required. I very much appreciate any help you can give me. If you have any questions or need further information please let me know. Thanks! | As I am understanding your situation, you will be installing a new engine and therefore, you it is considered new under the NESHAP (constructed at major source > 500 HP after 12/19/02). That being the case, the only requirement under the NESHAP is to submit an initial notification. See the introduction to the attached guidance document and page 65. You will have to comply with the NSPS for IIII or JJJJ depending on if it is compression or spark ignition. If you have questions about those requirements, I encourage you to talk to Stephenie Moyer at 402-471-0019 or at stephenie.moyer@nebraska.gov. As far as the construction permit goes, you will need to get a construction permit and most likely conduct modeling. I encourage you to call the permit hotline with questions at 877-834-0474. Or, you can contact our new Air Assistance Coordinator, Tim Kalb, at 402-471-3139 or at tim.kalb@nebraska.gov.
2010-11-02 | GMG Envirosafe | Distributor | NESHAP 6H | Joe Hayes | Cell: 847.274.5326 Office: 847.441.5137 jhayes@gmgenvirosafe.com | For a shop to qualify for exemption they must have all products below the NESHAP threshold level or do all their spraying in 3 oz or smaller cups. Correct? If a shop removes all non-NEHSAP compliant products from its inventory, can it order a pre-mixed product and spray the premix in their approved booth and still be compliant? What if the premix is below the threshold level? Above? Unless a shop receives an approved exemption or does all its spraying in 3 oz cups or less, effective January 2011 all spraying (compliant and non-compliant products) must be done within an approved booth or prep station. Correct? | Your first statement is correct. For a shop to qualify for exemption they must have all products below the NESHAP threshold level or do all their spraying in 3 oz or smaller cups. If the premix product contains the metal HAPs above the thresholds, they cannot use it if they are exempt from the rule. If they use product with the metal HAPs above the thresholds, all aspects of the facility need to be in compliance and they will be subject to the rule from then on. Unless a shop receives an approved exemption or does all its spraying in 3 oz cups or less, effective January 2011 all spraying (compliant and non-compliant products) must be done within an approved booth or prep station. This is correct, except that they can comply with the rule and have some cups 3 oz or less and use them outside of a booth and still be compliant. For instance, comply with all aspects of the rule and spray vehicle subassemblies with primer outside of a booth using cups with 3 oz or less.
2010-10-07 | GMG Envirosafe | Distributor | NESHAP 6H | Joe Hayes | Cell: 847.274.5326 Office: 847.441.5137 jhayes@gmgenvirosafe.com | I appreciate your patience. Based on previous conversations and emails, here's what I understand is required in regards to spraying in NE collision repair businesses: For a shop to get an approved Petition for Exemption it can either Remove all non- compliant products from the shop, or Only use 3 oz cups for all spraying of both NESHAP compliant and non-compliant products. Having larger than 3 oz cups in the shop would be evidence of violating an exemption. The alternative to Exemption is Compliance Certification. In regards to spraying, this requires (among other things) all products sprayed in an approved booth or prep station (with complete roof) unless it is done in 3 oz cups. The larger cup capacities are only available for use in a compliant booth or prep station. | That looks correct to me with one minor point. If a facility is only spraying out of 3 oz cups or less, they don't have to apply for a petition for exemption, they wouldn't be subject to the regulation at all. A petition for exemption is granted for utilizing non-target HAP paints at auto body shops.
2010-08-24 | D & R Auto Paint and Supply | Distributor | NESHAP 6H | Kevin Maher | Kevin Maher (402)-740-3910 kevin@drautopaint.com | rock chip & small scratch touch-up systems. They have automotive paint toners that are mixed & then applied by brush or wiped on. They are not sprayed or atomized in any way. They come in a kit with approximately eighty 1 oz. bottles of paint. I’m sure some of the toners have some of the HAPS in them. These shops have our waterborne Envirobase paint for their spray paint system & are planning on filing an exempt status. My question is; Does having those brushed on touch up paint toners in the shop exclude them from being able to be considered exempt? | If you are spray applying paint with a gun cup that holds 3 oz. or less, you don't have to meet the rule requirements. It sounds like you are brushing or wiping the product on. That type of application is not covered by 6H and you wouldn't have to meet the requirements, only spray applied. Tim, any other thoughts?
2010-08-23 | NPPD | Source | NESHAP 4Z | Jason Vanek | Jason Vanek, P.E. Environmental Engineer Nebraska Public Power District E-Mail: javanek@nppd.com Office: (402) 563-5333 Cell: (402) 910-1717 Fax: (402) 563-5168 | I was reading through the “Who needs to complete and submit this form” section on the initial notification form and had a question about #4. New and reconstructed emergency and limited use engines >500 HP at major sources need to send in a notification. We have 2 emergency CI generators at our Beatrice plant that were installed in 2004. One is 275 HP and one is 1,135 HP. • Since the 1,135 HP engine was built after 12/19/02 and is at a major source it would be a new engine and therefore we would need to send in an initial notification, correct? • Since the 275 HP engine was started before 6/12/06 it is an existing source, correct? | The 1135 HP engine is new and would need to submit an initial notification. The 275 HP is existing and if it is truly an emergency engine, you would not have to submit an initial notification for it.
2010-08-20 | Fremont Utilities | Source | NESHAP 5D | Dick Svatora | 402 727-2642 Richard.Svatora@fremontne.gov | I do have questions/concerns about 6J and 5D Proposed Rules. Fremont's two smaller EGU's are greater than 100 mmBTU/Hr and burn PRB coal as the primary fuel. One Unit has a Coms and a Baghouse and the other just has a Baghouse. I'm not sure of what is a "Major Source" and "Area Source" but I would assume they are both Major Source. Would this be correct? If this is true, required stack testing and a CO and PM Cems would have to be installed? Also fuel analysis for Hg & HCL would have to be done monthly if not stacking testing? | Yes, they are major. Rule is only proposed, Yes for rest of proposed questions on requirements
2010-08-11 | Nebraska Petroleum Marketers | Distributor | NESHAP 6C | Tim Keigher | tkeigher@npcainc.com | I was wondering if you knew if when updating existing stations with the vapor recovery systems the single point vapor recovery is going to be an acceptable modification. I am in charge of our equipment and I have already bought the adapter for the dual vapor recovery system and now if this single point vapor recovery system is acceptable to those who make the rules I need to get some more fittings to be ready when the stations make their change. | For 6B: tanks with > 20,000 gallons capacity: use specified floating roofs and seals or a closed vent system and control device to reduce emissions by 95% For 6C: Tanks at sources with >100,000 gallon throughput they have to meet one of thefollowing: 1. Operate a vapor balance system installed prior to 1/10/08, that meets an enforceable State, local, or tribal rule or permit that requires, either a) Achieves an emission reduction of at least 90%, or b) Operates meeting the management practices specified below (#7). 2. Operate vapor balance system during storage tank loadings using the following management practices. a) Equip connections & lines with seal closures b) Vapor tight line from storage tank to cargo tank c) Cargo Tank pressure remains below specified settings d) Designed to prevent over tight/loose fittings e) Gauge well provided with submerged drop tube extending specified distance (see item 5) from tank bottom f) Use vapor tight caps for liquid fill connections g) Install pressure/vacuum vent valves on tank vent pipes at specified setting, and test initially and every 3 years h) Vapor balance system must meet static pressure test initially and every 3 years i) Dual-point (no coaxial) vapor balance systems for new GDF or tanks, and reconstructed GDF. 3. Vapor balance system demonstrated to achieve a reduction of 95% or better. I'm not sure what type of system he is talking about, but this is what the rule requires. If I understand he is talking about the dual-point system and that is required for new gasoline stations or new tanks at gasoline stations.
2010-07-06 | Benkleman Valley Farms | Source | NESHAP | Rod Damerol | 308-423-2031 | left message
2010-06-25 | Sidney Power Plant | Source | NESHAP 4Z | Dave |  | Engine requirements
2010-06-23 | Timpte | Source | NESHAP 6H & 6X | Jeff Struck | 402-367-3056 | NAICS Code doesn't fall into 6X list and do not refinish vehicles, but paint parts of subassemblies - subject to 6X or 6H | No - as confirmed by Leslie Werner (7/6/10) - sent in negative declaration for both 7/9/10
2010-06-23 | Falls City Power Plant | Source | NESHAP 4Z | Dave Aiken | 402-245-3521 | Asked if limited use engine >500 at area source has lesser requirements | Only that testing is reduced to every 5 years or 8760 instead of 3 years or 8760. Still have to follow emission limits, controls, etc.
2010-06-16 | Senaca Consulting | Consultant | NESHAP 6H | Blaine Kussatz |  | Private residence, refinishes less than 2 cars per year - subject? | No, exempt from 6H
2010-06-09 | NE Machinery | Distributor | NESHAP 4Z | Tracy Henke | 402-891-7656 TracyHenke@nebraska-machinery.com | The customer is the City of Cambridge. They currently have two units in question. Both units are existing stationary RICE engines, assuming this is also an Area Source, both units are greater than 500 HP, both were manufactured in Nov of 2000, and both are classified as "non-emergency". From what I can tell, we need to provide the following items. 1) limit the engine to 23 ppmvd CO at 15% O2 or provide 70% CO reduction 2) perform start up and maintenance as recommended by Caterpillar and keep the start up period to a minimum of 30 minutes. 3) Perform on site emission testing, per item 25, table 4 to subpart ZZZZ, #3 for stationary RICE non-emergency engines. I do have questions on this, please see below. 4) Continuously Monitor and record the catalyst inlet temperature and record the pressure drop across the catalyst once a month. 5) use ultr low diesel 6) install a CCV, closed crankcase ventilation system on the engine. Under the testing procedures (Item 25, Table 4, item 3) it lists methods 1 or 1A of 40 CFR part 60, appendix A. It also lists Method 3, 3A, 4, 320 and 10. I have tried to locate these (on both NDEQ's and the EPA's web sites) but I am having difficulty. I have also tried to locate the ASTM methods listed, but it appears as though these are not valid numbers (using their web site). I was wondering if you could point me in the right direction to this testing information. On another note, I also have one additional question that I probably have asked you before. I have another customer in Nebraska (municipality) that would like to install some used RICE engines that were manufactured in 2000. These would be classified as "non-emergency", since they want to curtail with them. Since the units were manufactured (or constructed) before July 11, 2005, are they subject to NSPS rules or NESHAP rules? Basically if a customer wants to install used units, is the construction date of the project based on the construction date of the engine or the construction date of the "installation"? If the construction date is based off of the "installation" date, then these units would be required to be up fitted with emissions requirements to meet 2007 or later models (per CI ICE Option #4). | The summary of compliance requirements looks right. They will also have to conduct subsequent testing every 3 years or 8760 hours. They also have to submit an initial notification (on our website under the Air Toxics Notebook) go to this link: . They also have to submit a compliance status notification after the performance test. The testing methods they are referring to can be found on the electronic cfr site at: http://ecfr.gpoaccess.gov/cgi/t/text/text-idx?c=ecfr&sid=a4d1379cc46309c702daa760c8562aa7&tpl=/ecfrbrowse/Title40/40cfr60d_main_02.tpl. On the other question - Under the NESHAP, they are considered an existing unit if the unit was installed or built on-site before 6/12/06. If the units were installed after that date, they would be a new source. The NESHAP regulates new and existing sources. Under the NSPS, you look at the date the unit was ordered and manufactured. If the unit was manufactured before 4/1/06 and not reconstructed after 7/11/05, they aren't subject to the NSPS. They would only be subject to the NESHAP. Does that help?
2010-06-08 | Yant Equipment | Distributor | NESHAP 6B/6C | Ron Arent | 308 382-5830 | called with questions regarding installing vapor recovery systems on new tanks and retrofitting existing tanks. He is specifically interested in whether or not coaxial systems were EPA approved as he is getting conflicting information. | I talked to Mr. Arent. He wasn't sure what the EVR was either (I think it is a CARB term), but from what we discussed we came up with the following: 1. He was referring to compliance with 40 CFR Subpart 6C for Gas Dispensing Facilities. 2. The requirement for facilities with a throughput greater than or equal to 100,000 gallons per day is that they have a "dual vapor balance system." 3. A dual vapor balance system under 63.11132 is a type of vapor balance system in which the storage tank is equipped with an entry port for a gasoline fill pipe and a separate exit port for a vapor connection. 4. He stated their equipment meets this definition and should meet compliance with the regulation. I gave Mr. Arent my number if he had any other questions. Let me know if you have any questions also.
2010-06-02 | Grand Island Utilities - Burdick | Source | NESHAP 5D | Emily Wise | 308-385-5495 | Want to moth-ball three boilers, wouldn't be ready to fire, water drained and couldn’t just startup - would they still need permit? Would they be subject to 5D or 6J still? | Clark said good idea to put into OP, wouldn't be subject to boiler rules anymore
2010-05-21 | Pittsburgh Paints | Source | NESHAP 7C | Randy | 712-737-4993 | Needed to know where to send initial notification to | Send to LLCHD
2010-05-20 | NE Machinery | Distributor | NESHAP 4Z | Tracy Henke | 402-891-7656 TracyHenke@nebraska-machinery.com | Called related to non-road engine determinations for portable rock crushers | Emailed Clark's draft applicability determination
2010-05-20 | Hyvee Gas Stations | Contractor | NESHAP 6C | Mary Thompson | 515-327-4908 | Installs stage 1 vapor recovery and sending in results and notifiations | Needs to send to LLCHD and to us - we don't have any notifications for HyVee
2010-05-19 | Hemingford | Source | NESHAP 7D | Jeff Kohl | 308-487-3317 | Questions related to EPA's Q & A related to primarily engaged | He will look at their production and send in letter with negative declaration if not subject
2010-05-17 | Dr. Vinyl | Source | NESHAP 6H | Doug Hancock | 402-592-1783 | Sent petition exemption to EPA R7 & hadn't heard back. Also wondering if they needed exemption for all portable vans | Getting paperwork from EPA R7. Only need exemption for facility not each person working for them.
2010-05-14 | OPPD | Source | NESHAP 6H | Jane Spires |  | Send notification to Omaha - sending to us - paint transformers - need to look at MSDS, but think they are subject
2010-05-14 | OPPD | Source | NESHAP 6C | Jane Spires |  | notifications for >10,000 gallons - sent to Omaha, but in Elkhorn and need to send to us
2010-05-13 | NE Machinery | Distributor | NESHAP 4Z | Tracy Henke | 402-891-7656 TracyHenke@nebraska-machinery.com | New requirements for existing engines | Email info
2010-05-05 | Les Hoffman - Body Shop | Source | NESHAP 6H | Les Hoffman | 402-934-2793 | Questions related to 6H requirements | In OAQC jurisdiction, gave him Tim Burns info also showed him Air Toxics Notebook
2010-05-05 | NMPP | Source | NESHAP 4Z | Kevin Gaden | kgaden@nmppenergy.org | Worried about municipalities with existing engines > 300 HP | Kevin, The rule only generalizes nationwide costs, not per control unit. Instead, it refers you to the regulatory impact analysis found in the rulemaking docket. The first link has everything in the rulemaking docket. The second points to the regulatory impact analysis, which will be the most helpful. See page 72 for their equation. Also, I've included a link to a verified control technologies document that might be useful. http://www.regulations.gov/search/Regs/home.html#docketDetail?R=EPA-HQ-OAR-2008-0708 http://www.regulations.gov/search/Regs/home.html#documentDetail?R=0900006480aa6b64 http://www.regulations.gov/search/Regs/home.html#documentDetail?R=09000064808dabb3
2010-04-26 | Compliance Advisory Services | Consultant | NESHAP 7D | Doug Salmon | 402-984-1104 | Questions related to baghouse on operations and pelleting productions. Letter from EPA??? | Leslye Werner - calling HQ - didn’t send letter
2010-04-16 | Watson Motor | Source | NESHAP 6H | Karen | 402-582-4211 | Questions related to forms, rule, etc. Showed her website information and explained summaries to look at.
2010-04-15 | RP's Body Shop | Source | NESHAP 6H | Rock Premer | 402-756-2957 | Sent in letter with initial notification stating they think they are in compliance. They also said they will be moving to water based paints and wanted to know how they notify us of that. | Left message 4/15/10. Mailed petition exemption form 4/119/10
2010-04-14 | Bosselman's | Source | NESHAP 6C | Dave Korgel | 308-384-8830 dave.korgel@bosselman.com | How/what method does a source use to notify that they are not >100,000 as originally notified? What if they go above 100,000 and didn't notify that they were > in initial notification? | Call to Bill Peterson. Emailed information to Dave 4/21/10: There isn't a requirement in the regulations for a facility to contact us when they are below a threshold. Even though a notification wouldn't be required, I'd recommend one, if the compliance date hasn't passed. Only as informational purposes. This is so we know which "bigger" sources we have an may need to inspect, etc. It will also keep your files current. However, in the 12/2009 rule proposals, EPA clarifies that once a facility goes over a threshold, they will always have to comply with the higher threshold after the compliance date - even if they go below later. If they go above a threshold, they are required to send in a notification.
2010-04-14 | Great Dane Trailers | Source | NESHAP 6H | Craig Tentinger | 402-375-5500 | Sent in 6H exemption. Not sure if they are subject. Asked Leslye Werner with EPA 1/8/2010, but no response. They only paint part of the truck trailers when it is subassembled. | Call to Leslye. -OK to approve petition exemption. Petition exemption to bev/shelley 4/16.
2010-04-08 | DOR | State Agency | NESHAP 6C | Belinda Fowler | 479-4656 | DOR has facilities >10,000 gallons in Omaha, OAQC wants to charge them inspection fee, they don't think they have to pay | not our jurisdiction & not sure how that would work

## Determinations and Policy
Date | Who's Asking? | Subject or Subpart | Contact name | Contact info | Question or Issue Description | Answer and/or Follow up
2012-04-10 | Adam Yarina | NSPS 2D | Adam Yarina |  | Dan LeMaistre had a question about a grain elevator he is writing a permit for. The grain elevator in question is capable of processing 427,000 tons of grain, or about 8,820,000 bushels. There is also a feed mill (animal food manufacturer) on-site, capable of processing 50,000 tons of feed, or about 12% of the grain elevator’s throughput. My interpretation of the subpart is that the grain elevator falls under the definition of “grain terminal elevator,” as defined by 60.301 (c), due to its throughput being greater than 2.5 million bushels. While the definition excludes grain elevators located at animal food manufacturers, it seems to me that this exclusion does not apply, since the facility is overwhelmingly used for grain processing. In other words, this is more a case of “animal food manufacturer located at a grain elevator,” rather than “grain elevator located at an animal food manufacturer.” Is this correct? | Ward Burns of EPA R7: Elevator is not subject to NSPS DD because there is an animal feed mill located at the same site and owned by the same company. Even though the feed mill is not the primary business and constitutes only a small portion of the grain elevator's throughput, there is nothing in the rule that specifies a threshold for any of the activities that exempt facilities from NSPS DD (in this case, the presence of an animal feed mill).
2012-06-04 | Melissa Ellis | NESHAP 4Z | David Peter | 913-551-7397 David Peter Peter.David@epamail.epa.gov | Hi, David! We had a few questions or clarifications regarding the NESHAP 4Z proposal. Can an engine accept capacity credits from their distribution organization and still be considered emergency (until 2017)? This would mean they have a non-interruptible service contract. The rule allows 50 hours of non-emergency operation to be used for non-emergency demand response while generating income. I think the capacity credit scenario fits into this, but wanted to be sure. Also, many municipalities don’t know if they are operating in an emergency demand response situation or a non-emergency demand response situation. They just operate when they are asked to do so. How are they suppose to keep track of this? Especially since they have more time allowed to operate under the emergency demand response and low voltage. This creates a recordkeeping/compliance demonstration issue for them and us. I think it would be easier to keep track of peak shaving hours because they typically choose when to operate during those times. Any thoughts on this? It might be something we’ll have to comment on for clarification, but I thought you may have some insight. | For your first question, this situation appears to meet the definition of peak shaving to me and the engine, like you mentioned, would be allowed to operate for 50 hours per year for this purpose under the current proposal and the engine would still qualify as emergency until 2017. For your second question, I am planning on talking to the Region 7 municipality organizations over the next couple of weeks to ask them some of these and other questions. It is my understanding that when a municipality operates to maintain a certain voltage level, the municipality does so based on some set of criteria (like a 5% voltage drop) and is not necessarily ordered to do so by an RTO. The current final rule requires the demand response operation to be ordered by an RTO. I believe that the new 5% voltage drop language was included to address this situation for municipalities. In other words, it is my understanding that these municipalities will not normally operate under a "demand response program" (as discussed in the proposed rule at 40 CFR 63.6640(f)(ii)) but will normally operate under the 5% voltage drop situations (proposed regulation 40 CFR 63.6640(f)(iii)). The owner or operator of emergency generators are required to maintain records of operation in accordance with 40 CFR 63.6655(f). The current rule addresses maintaining records for periods of "emergency operation" and "non-emergency operation". For "emergency operation", the owner is required to record what classified the operation as emergency. For "demand response" operation, the owner is required to maintain records of the notification of the emergency situation (from an RTO) and the time the engine was operated for this purpose. The current and proposed rule doesn't address "low voltage" operation. It does appear that 40 CFR 63.6655(f) would need to be revised to address "low voltage" operation record keeping. I would assume that the owner would need to provide some sort of documentation for the rationale for "low voltage" operation (such as records showing a 5% voltage drop) and the time the engine operated for low voltage purposes.
2012-05-29 | Melissa Ellis | NESHAP 4Z | Gary Bertram | bertram.gary@epamail.epa.gov | Does a landfill have an SSM plan and follow it? And, if they don’t follow it, would it be a violation? | I took a look at your question and the vacature does not appear to affect the Part 63, Subpart AAAA SSM Plan requirement. Here's what I noted: - The vacature affects 40 C.F.R. Sections 63.6(f)(1) and 63.6(h)(1); - The AAAA requirement at 63.1960 refers back to 63.6(e)(3); - 63.6(e)(3) provides criteria for SSM plan; - 63.6(3)(3) makes no references to 63.6(f)(1) or 63.6(h)(1). The vacature focuses on SSM events and does not appear to affect the requirement for landfills to prepare an SSM plan.
2012-04-18 | Melissa Ellis | NESHAP 4Z | David Peter | 913-551-7397 David Peter Peter.David@epamail.epa.gov | One of our facilities has an engine that predominantly uses biodiesel with No. 2 as a back-up. Their air permit states that No. 2 diesel is worst case scenario and they can demonstrate compliance with their limit be testing only No. 2. How does this work for the NESHAP 4Z? Do they have to test both? Can they test worst case? Does EPA agree that No. 2 would be worst case? Your help is appreciated. | The engine would have to meet all applicable emission limits during combustion of all fuel types. EPA has generally determined that the combustion of biodiesel results in lower emissions than the combustion of No. 2 fuel oil. CO & air toxic emissions appear to be slightly lower when combusting biodiesel and NOx emissions appear to be slightly higher (see http://www.epa.gov/otaq/renewablefuels/420f10009.htm#6, among other EPA informational sources). I would think that EPA would agree that testing on No. 2 fuel oil would be the worst case fuel. If the engine is greater than 500 hp, we could ask them to test on both fuels for their initial test to prove they meet the limit using either fuel. After that we could allow them to conduct subsequent tests on only one fuel. For the initial test, we could even consider a shorter test on the second fuel so they don't have to do two tests of three 1-hour runs each.
2012-01-03 | Melissa Ellis | NESHAP 4Z | David Peter | 913-551-7397 David Peter Peter.David@epamail.epa.gov | One of our nuclear plants has emergency engines that are required by the NRC to perform testing and maintenance greater than 100 hours during some years. Section 63.6640(f)(1)(ii) states: The owner or operator may petition the Administrator for approval of additional hours to be used for maintenance checks and readiness testing, but a petition is not required if the owner or operator maintains records indicating that Federal, State, or local standards require maintenance and testing of emergency RICE beyond 100 hours per year. In this case, I do not think they need to petition us as long as they have the specifications from NRC to operate greater than 100 hours per year. Is this your interpretation? | I agree with your interpretation. The NRC is a federal agency that could require the engine to operate more than 100 hours for maintenance checks and readiness testing. In fact, the NRC requirement to operate more than 100 hours came up in EPA's 2/17/2010 response to RICE MACT comments (pages 191-194). As you indicated, the facility would only need to maintain some sort of record indicating the NRC required more than 100 hours.
2011-12-13 | Gary Bergstrom - LLCHD | NESHAP M | Melissa Ellis |  | Where is the requirement to remove transfer machines? | Gary: Looks like the citation for eliminating transfer machines is 63.322(o)(3). The preamble of the rule clarifies. Let me know if you have any other questions! C. What Are the Requirements for Transfer Machines at Existing Major and Area Sources? The final rule prohibits the use of all existing transfer machines two years from the effective date of the final rule by requiring owners or operators to eliminate any PCE emissions from clothing transfer between the washer and dryer. The installation of new transfer machines was prohibited by the 1993 Dry Cleaning NESHAP.
2011-11-15 | Melissa Ellis | NESHAP A | Angela Catalano | catalano.angela@epamail.epa.gov | Ash Grove requested an extension for the new compliance requirements in Subpart LLL. We had not adopted the changes to Subpart 3L and didn't believe we had the authority to extend the compliance date. | Our legal staff and EPA's legal staff determined we could provide a compliance extension to requirements not found in T129. This is because we are delegated the authority under Subpart A. Explanatory documents in file.
2011-10-26 | Melissa Ellis | NESHAP 4Z | Eric Sturm | sturm.Eric@epamail.epa.gov | 1. I understand it is allowed to have a financial agreement in place to pay an engine to operate under emergency conditions. Is it also allowed for an engine to receive payment for operating during testing, maintenance, and demand response? Also, who will determine whether a situation is demand response or peak shaving? There seems to be a grey area in the definitions. Will the demand response reconsideration address this? 2. My understanding is that pressure drop across the catalyst cannot differ +/- two inches from the tested value. Some sources are under the impression that they just can’t be above the tested baseline by more than two inches, but they can be below. The sources stated that if they are only at 50% load, the pressure differential will vary greatly from the baseline at 100% load. From my understanding, they are only supposed to record the pressure drop when operating at the tested load of (100% +/- 10%). Can you help me understand this better? | 1) Yes. Financial arrangements are allowed for emergency engines at area sources to be paid for testing and maintenance to be a part of a demand response program. The implementing agency with delegated authority (NDEQ then EPA) would decide the demand response or peak shaving. Of course, the company will have to provide the information to you to decide that. I brought up this question with our rule writers. They couldn't discern between the demand response and peak shaving operation. I asked, "If you don't know how to, how will the company or states that have to implement the rule be able to?" That may or may not have led to the Oct 18 letter I sent you where they've decided to reconsider whether peak shaving should be allowed for some emergency engines. 2) I'll need to look at the preamble, but I think the rule is clear how the pressure drop must be met. Like you point out, +/- 2 inches H2O from the tested value. Instead of saying "baseline", let's say tested value. I don't follow what's meant by baseline in this case. So, if the source is operating at 50% load, and the pressure drop has decreased below 2 inches H2O the tested value - then the source has no data to show that they're in compliance. Simply, CO ppm goes up when pressure drop goes down across a catalyst. Maybe first of all, engines aren't expected to operate at the 50% load level. If the source will be operating at the 50% load level for extended periods (like in the range of hours similar to how the standard must be met), then it might make sense for the source to test at that load level along with the 100% load test to show the % CO reduction across the catalyst is still being met. My understanding isn't that the pressure drop only needs to be recorded when operating at 100% load. But, I might be wrong and maybe we should talk more. Of course, the source is allowed 30 minutes of startup where they don't need to record the pressure drop, but after that, when the engine continues to operate, I've read that pressure drop recordings need to be made to assure the standard is being met.
2011-09-20 | Melissa Ellis | NESHAP 6J | Lisa Hanlon | Hanlon.Lisa@epamail.epa.gov | Can you tell me how/if boilers burning tallow, animal fat, and vegetable oils fit into NESHAP 6J? We made a comment to the proposal (see below) and didn't see it addressed in the final preamble. Can you tell me if they would be considered biofuels, liquid fuel, or solid waste? Several facilities in Nebraska operate boilers which combust tallow, white/yellow grease, and vegetable oils. The fuels are typically byproducts from animal processing and rendering plants. NDEQ encourages facilities to burn these fuels to minimize the amount of traditional fossil fuels combusted. These are considered secondary materials and meet the proposed criteria for legitimate fuels as referenced in the June 4, 2010 Federal Register proposal (75 Federal Register 31844). They do not meet the definition of a non-hazardous solid waste. Because these fuels have similar emission characteristics as biodiesel fuels, and are cleaner than diesel in most respects, they should be included within the liquid fuel definition and regulated similarly to boilers combusting those liquid fuels under the National Emission Standards for Hazardous Air Pollutants. | I still haven't heard from Jim Eddinger, so with a lack of HQ guidance, I am going with my reasoning that this is a liquid fuel. The definitions in the area source MACT seem to me to be indicative of liquid fuel. I think we're both right on this one.
2011-09-20 | Anne Pamperl | NESHAP 6J | Melissa Ellis |  | what did USEPA decide to do about waste oil heaters? Darling International has a small one: 150,000 Btu/hr, 1250 gal/yr waste oil throughput. | It should be included in the liquid fuel category as long as it isn't defined as waste. You may want to talk to Stephenie about how this ended up in the CISWI (although it is stayed, I think). From the proposal, I remember that EPA was defining "off spec" oil as waste and "on spec" oil as a fuel. If it is considered waste, they would have to comply with the CISWI and not 6J.
2011-09-20 | Melissa Ellis | NESHAP 6X | Joe Terriquez | terriquez.joe@epamail.epa.gov | We have a facility with a SIC code of 3499 that manufactures automobile seats. Their corresponding NAICS code is 336360. 3499 is listed on EPA's table of applicable codes for 6X, but 336360 is not listed. Are they subject to 6X or not? | To answer your question they would not be subject, the SIC and NAICS codes both have to be covered.
2011-09-13 | Melissa Ellis | NESHAP 4Z | Melanie King | King.Melanie@epamail.epa.gov | We have an area source with 4-stroke rich burn engines that are >500 HP. They predominantly burn digester gas and burn natural gas as a supplement. Eric Sturm (Region VII) indicated we have significant discretion to allow a facility to comply with the predominant fuel requirements, since NESHAP Subpart ZZZZ is silent regarding predominant fuels. Our permitting and compliance staff decided engines that consume 80% of their total annual fuel usage as landfill or digester gas will comply with the landfill/digester gas requirements. If their consumption of natural gas exceeds 20% of the total annual fuel usage, they will be required to comply with the natural gas requirements. We are implementing this strategy by including the 80/20 fuel requirements in their operating permit, unless we hear otherwise from EPA Headquarters. | Hi Melissa, thanks for the heads-up, I don't have any issues with this. I recognize that it would be a good idea to clarify this issue in the rule, so we may do so at some point in the future if we're making changes to the rule.
2011-08-29 | Melissa Ellis | NESHAP 4Z | Eric Sturm | sturm.Eric@epamail.epa.gov | We have a situation where a facility has 3 engines that are 4-stroke rich burn > 500 HP and burn digester gas and natural gas. The requirements for digester gas engines are maintenance, but for natural gas they have to comply with emission limits. Which do they comply with? They mostly burn digester gas, but the rule doesn't mention "predominant" fuels. | You won't find a distinct ratio for NG to digester gall to determine the applicable standard. I think the PA has some significant discretion to decide which standard should apply based on fuel, operation, use, and location of the engine. Responses to comments for the NESHAP and NSPS state that if 10% or more of the fuel burned is digester gas, then digester gas engine standards should apply. NSPS JJJJ might call out that ratio, but I'm not sure. Either way, I've requested to Melanie that it be in all future engine rule makings.
2011-08-22 | Melissa Ellis | NESHAP all |  |  | If a facility submits an initial notification saying they are subject to a NESHAP, but our analysis shows that they are not subject, what course of action should we take? Should we just allow the facility to comply (assuming that they know something we don't) or just tell them flat out that they have been doing all sorts of extra work? | They should submit a letter to us stating that they aren't subject and the reasons they've come to that conclusion so that we have documentation. They shouldn't be on our list or have to comply if they are not truly subject.
2011-08-03 | Melissa Ellis | NESHAP 6C | Bill Peterson | peterson.bill@epamail.epa.gov | I have a question on NESHAP 6C for Gas Dispensing. We have a facility (Offutt Air force Base) that has several locations on their property for dispensing gasoline. It appears the rule recognizes this (63.11111(h)) as it states….."If an area source has two or more GDF at separate locations within the area source, each GDF is treated as a separate affected source." The only part of the preamble amendments of 1/24/11 that mentions it is on page 4167 #4, but there is no discussion about it. My question is how do you determine if it is considered a "separate location?" Is it a rule of distance? We just want to be sure we are looking at the facility correctly in a permit. We wouldn't want someone to come back at a later date and say they should have done it differently and thus their throughputs are over 100,000 gallons etc. Your input is appreciated! | Response was a copy of the proposed rule amendments preamble 12/15/09, page 66479. Each location would be considered a separate GDF and there is no distance/spatial requirement.
2011-07-27 | Melissa Ellis | NESHAP 6X |  |  | Sent to Clark, Shelley, Todd, & Bev: I received the following from Nucor Cold Finish. They are requesting we make a determination regarding whether or not they are subject to NESHAP Subpart XXXXXX for Metal Fabrication. My thought is that EPA should be making these decisions, but I wasn't sure of the procedure. This is the rule EPA has advised us to implement in a way inconsistent with the regulation. Does the source need to send it directly to EPA? Does it go to Region VII or Headquarters? Any help you can provide is appreciated!Sorry, it has been a while since we've talked about it (probably 2 years+). EPA has advised (Headquarters and Region 7) that a source would have to fall into the 9 listed NAICS codes to be subject to the rule. The NAICS codes are not in the regulation text. Nucor's question relates directly to the NAICS code issue. If you read the rule, it would seem there are a lot of sources subject. EPA has repeatedly told us and sources that if your NAICS code doesn't fall into the list they've compiled, that the source isn't subject. | From Shelley 7/27/11: Do we have that in writing from EPA? I kinda recall that issue now…. If we don’t have it in writing, we could slap a cover letter on the letter from Nucor Cold Finish asking EPA to provide us with written clarifying guidance on applicability as it pertains to NCF. Pulling out whatever we can in the rule/preamble/etc…. that speaks to applicability. Thoughts? From Melissa 7/28/11: They have it in writing in a Q & A publication (attached). Would that be sufficient? Melissa 8/11/11: I hadn't hear back from anyone on my last response, so I'll ask the question again. EPA does have a Q & A document on their website that seems to answer their question. Is that sufficient for me to respond and point to their document? Or, should we send it to EPA for their response? Clark 8/11/11: I think that Shelley did the same thing I just did with Brad – used ‘could’ instead of ‘should’. Based on her response, I would just send it to EPA.I have been playing catch up Melissa from being on funeral leave. Shelley 8/11/11: I do not recall seeing a response to my note of the 27th. Melissa 8/11/11: I know you have been gone, sorry, didn't mean to seem like I didn't understand. Others have been here and no one responded (only you, earlier). Thought others could have helped me out with this, but no one wanted to. I had responded to you (I didn't save the note). I think it was before you left for the NACAA trip. Anyway, EPA has the attached Q & A document on their website. Should I use this information and respond or should EPA be answering this type of question? Thanks! 10/19/11 - recieved phone call from Nucor Cold Finish, Dwight Eisenbraun asking about determination. Told him my administrator had not given me the go ahead to respond to the letter or do anything with it. They will have to talk to EPA. Gave him Joe Terriquez number. I stated the Q & A document answers their questions, but since EPA has told us to implement the rule differently than regulation - they would have to be the one who answers the letter.
2011-06-17 | Melissa Ellis | NESHAP 5U & 6J | Lisa Hanlon | 913-551-7599 | A 25 MW natural gas boiler won't be subject to requirements in 5U, would they be subject to 6J? | No, it is a utility boiler and wouldn't be subject to 6J.
2011-06-15 | Melissa Ellis | NESHAP 5Y | Leslye Werner | Werner.Leslye@epamail.epa.gov | 1. Initial Notifications - The EPA brochure doesn't mention that one is required. However, the rule references that Subpart A 63.9(b) applies. My thought is that a notification was due for existing sources by 4/26/08 (120 days from effective date) and within 120 days of startup for new sources. Is this correct? 2. Compliance Status Notifications - The EPA brochure says they are due by 6/30/08 or 60 days after a test. But, the rule just references 63.9(h). 63.9(h) requires compliance status notifications be submitted within 60 days if there is a test or 30 days if there is just an opacity or VE observation. It doesn't say anything about requiring the notification on the compliance date, which is 6/30/08 in this case. What is your thought on this? My thought is that it is due at least 30 days from the compliance date if there is no test required. | Leslye: I agree with both your interpretations of 5Y.
2011-05-31 | Melissa Ellis | NESHAP 4Z | Clark Smith |  | I'm doing a presentation for Interstate Power Systems & Lyman-Richey. I'm sure we'll discuss stationary vs. non-stationary. If the plant has the capability to connect to the grid or use an engine and decide to connect to the grid - is the engine still considered stationary? I read the new draft guidance and am now confused. I also had some questions about the draft guidance statement about the once in always in policy. | If I remember correctly, if the temporary stationary source (portable) does not have an engine dedicated to it, i.e., permanently attached, then all engines associated with it are nonroad engines. On the other hand, if the portable has an engine dedicated to it, then that engine is always a stationary source. Even if they decide to hook up to the grid and not use the engine, the engine remains a stationary source. The once-in-always-in issue is a little tricky and may be one of the reasons why EPA has a different interpretation than we do on engines at temporary sources. Normally, I would say that once an emission unit is subject to a NESHAP, it is always subject. However, with engines that becomes difficult because of the CAA. As discussed in our guidance and supporting memo, the CAA prohibits States from placing requirements on nonroad engines and a nonroad engine is clearly defined. So, when an engine is removed from stationary source use and placed in nonroad use, we cannot use the once-in-always-in policy to say that ZZZZ still applies to that engine. That is, a statute would clearly trump a policy. I’m sure that EPA would not have a problem with this interpretation for temporary sources. They already say that an engine dedicated to a temporary source is a nonroad engine due to the portability of the temporary source. There is a very slim chance that EPA would push back on this interpretation for an engine at a regular stationary source. However, as pointed out above, it would be difficult to justify their policy trumps a statute.
2011-05-26 | Olsson Associates | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov | We are looking at purchasing portable equipment which has capability of monitoring one stream at a time only. Seems to me that we should be able to run 3-1 hr tests on the inlet, 3-1 hr tests on the outlet and use that data to input into the equation. I don’t see anywhere in the equation or regulation that states the inlet must be monitored at the same time as the outlet. As long as the engine is operated at the same rate, load, etc. there should not be any difference. If we have to monitor the inlet/outlet simultaneously we would need to purchase two pieces of the same equipment. We may purchase two analyzers anyway to reduce on-site time, but we do want to know what our options are as the equipment is very expensive. | I understand your concern here. The portable analyzers can be very costly. Reading the requirements under § 63.6620, I think it's fairly clear that the tests for inlet and outlet concentration were meant to be done at the same time, but I see your point. In responding to comments about the rule, EPA believes that there are too many variables, like the ones you mention, to allow sequential testing for the percent reduction. See http://www.epa.gov/ttn/atw/rice/rice_rtc_2-17-10.pdf and excerpted below. Specifically, changes in load, temperature, or fuel type may effect the emissions testing. There are options to petition the Administrator for alternative performance testing. That would be something you could consider although it would be difficult to get an alternative approval where EPA has already supplied a response. "9.0 Compliance 9.1 Test Procedures 9.1.1 Comment: Several commenters (97, 112, 155, 224, 227, 242) recommended that EPA allow sequential pre and post-catalyst testing instead of simultaneous testing for engines complying with the percent reduction option. FTIR testing is expensive and will be a significant burden, but if sequential pre and post-catalyst testing is allowed the cost can be minimized. According to commenters (155, 242), most owners/operators will choose to comply with the percent reduction standard and not the concentration standard. Commenter 242 noted that this is because the level of the ppmv standards is very stringent and is exacerbated by the high percent efficiency that EPA has assumed. The commenters (155, 242) suggested that EPA allow sequential pre and post-catalyst testing for formaldehyde and CO percent reduction, while also prescribing practical quality assurance measures (e.g., engine load monitoring) to make sure that the sequential measurements before and after the catalytic control device are conducted at similar engine operation. Response: EPA does not believe the use of sequential pre and post-catalyst testing is appropriate for measuring percent reduction for a compliance standard. There are too many variables in the operation of an engine and the generated emissions to ensure that the percent reduction was being achieved. Changes in load, temperature, or fuel type can change during the test, which also affects the emissions. " In regard to performance testing for the RICE MACT, the requirement is to run simultaneous tests across the catalyst to determine percent reduction according to § 63.6620. I'm fairly certain Nebraska and Kansas read the rule the same way, but you might want to check with them to make sure. § 63.6620 What performance tests and other procedures must I use? ... (d) You must conduct three separate test runs for each performance test required in this section, as specified in §63.7(e)(3). Each test run must last at least 1 hour.
2011-05-25 | Anne Pamperl | NESHAP 5U | Melissa Ellis |  | Missy - I know USEPA has issued a stay that affects the revised CISWI rule, but I'm wondering what USEPA had intended prior to the stay, if anything, for a large coal-fired power plant that mixes used oil with its coal and then combusts the coal/oil in its boilers. The power plant in question is Gerald Gentleman Station, and the used oil is generated by NPPD's vehicles and those of employees. | It depends on whether the oil is 'on spec' or 'off spec.' If it is 'on spec,' it would be considered liquid fuel. Then, you would look at how much they burn on an annual heat input basis to determine which subcategory they fall into. On-spec used oil meets the requirements in 40 CFR Part 279. Yes, the citation and information were helpful. I went to 40 CFR 279 and found that 279.12(c)(2)(i) allows utility boilers to combust off-spec used oil, so NPPD should be ok whether the oil is on or off spec. So far as I know NPPD does no testing but is careful about the sources of the oil combusted. The preamble to the rule states that EPA is not reopening Part 279, and at one point singles out 279.12(c)(2)(i) in the discussion. A review of the final rule isn't as clear. NPPD treats the used oil as a valuable item/fuel, so they probably fall under 241.3(d)(2)(i).
2011-05-17 | Melissa Ellis | NESHAP 5Z | Pat Scott | (913) 551-7312 | Are all facilities required to submit semiannual deviation reports? The rule references to submit reports in accordance with 63.10(e). When I look at that section it states it applies to additional reporting requirements for sources with continuous monitoring systems. It doesn't seem like this would apply to small foundries, but I'm not sure. | From EPA HQ - Conrad Chin OAQPS: It was a typo and a wrong reference to 63.10(e)..... it should have been 63.10(d). Small foundries are not required to have CMS. Semiannual compliance report is required for both large and small foundries. The report includes deviations. Semiannual report is required even when there are no deviations, even if it just simply stating the source is meeting all the scrap/mercury management requirements.
2011-05-09 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov | A facility is buying a used engine mfg. in 2001. They will be considered an existing source. When are they required to submit an initial notification? What is their compliance date? Under any other rule, they would have been considered new and comply upon startup up, send in the notification within 120 days, etc. But, since this rule is different, I'm not sure how it is supposed to work? I am pretty sure this will be a common scenario and will occur after May 2013. | Interesting. I guess I don't read the rule to be different than other MACTs in these situations. The engine would comply with the MACT either upon startup or the compliance date - whichever is later. Say it starts up a week from now - the compliance date would be May 2013. For initial notification, still submit if required under the rule. The source would have 120 days after startup to submit the initial notification. 63.9(b)(2) states 120 days after the area source becomes subject to the relevant standard. They've said an engine that is existing (but will be new to the facility) has to be in compliance by May 3, 2013. If they start up after that date, they must be in compliance upon startup. The initial notification is due 120 days after startup. Let me know if you have any other questions!
2011-04-13 | Clark Smith | NESHAP 3E | Melissa Ellis |  | Are we the Administrator for purposes of Subpart EEE? Siew suggested that we add some language to the Clean Harbors permit regarding a notification required under Subpart EEE. Her language says the notification must be submitted to the Department 60 days before the test, however, Subpart EEE states it must be submitted to the Administrator at least one year before the test. If we are the Administrator, we have to go with the one year language. If EPA’s the Administrator, then we can get by with the 60 day notice, but remind them this requirement does not relieve them from the one year EPA notification. Hope that made sense. The requirement is in 63.1207(e)(i). | Each NESHAP has an Implementation & Enforcement section (see below). So, it looks like we have been delegated this part of Part 63. I'm not sure if the permit distinguished the difference, but the rule discusses a Comprehensive and Confirmatory test. The comprehensive test requires one year notice and the confirmatory requires 60 days notice. They have to follow what the rule says even if it was incorrect in the permit.
2011-04-12 | Melissa Ellis | NESHAP 6J | Lisa Hanlon | Hanlon.Lisa@epamail.epa.gov | Subpart 6J - Area Source Boilers 1. Does 63.11226 (Affirmative Defense) only apply to those subject to emission limits? 2. Is the fuel analysis required for anyone subject to an emission limit or those subject to a Hg limit? 63.11211(a) states it is for all subject to an emission limit. 63.11213(a) states only those subject to the Hg limit. Who actually needs to do the fuel analysis? Those burning a single fuel don't have to do it? Or do they? If you are doing fuel analysis, you don't have do any stack testing - correct? 3. 63.11220 states subsequent tests are required every 3 years. Then, it goes on to say it can be less frequent if you are less than 75% of the limit, but it says the frequency is still every 3 years. Is this a typo? Can the frequency be reduced? 4. 63.11210 - When is the initial compliance demonstration for the fuel analysis required? 180 days after the compliance date like stack testing? 5. 63.11225(a) - Compliance status notification - says 120 days after compliance date or 60 days if you have to test. For existing sources, there are two compliance dates - one for startup/shutdown & tune-ups and one for the energy assessment & emission limits. Are two compliance status notifications due in the case they are subject to both dates? Or is it the later of the two dates? 6. 63.11223(c) - only applies to existing/new coal > 10 MMBTU/hr, but Table 2 says this applies to new oil & biomass. Is there a typo? I'd assume Table 2 is correct and it was unintentionally left out of 11223(c). 1. The definition for coal subcategory includes a boiler burning any solid fossil fuel and no more than 15% biomass. The biomass subcategory includes any boiler that burns at least 15% biomass. What if a unit is burning 15% biomass, which subcategory would they fall into? Each seem to include 15%. The major source rule is clear in that is says a unit that burns at least 10% and less than 10%... I'm assuming it is the same intent for this rule and that the coal should say less than 15% biomass, but want to be sure.
2011-04-12 | Melissa Ellis | NESHAP 6J | Lisa Hanlon | Hanlon.Lisa@epamail.epa.gov | 1. Who has to do the fuel analysis? All subject to emission limits or just those using to comply with Hg and HCl limits? 63.7510(a) says all and 63.7521 says for Hg and HCl. If they are conducting fuel analysis for Hg & HCl, is testing required? 2. Are output-based limits available for both new and existing sources or just existing? Do they still have annual testing if using output-based to comply? 1. If a source is required to install a PM CEMS, are they exempt from the requirement to test annually (except for quarterly RATAs) and to follow operating parameters? I think this is the case, but wanted to double check. 2. When does the initial fuel analysis have to be conducted? within 180 days of the compliance date? 3. 63.7530(b) and Table 7 require measuring pressure drop, pH, and flow rate from the wet scrubber. However, Table 4 only says pH and flow rate. Which is correct? 4. 63.7515(g) says to submit reports of performance tests and fuel analyses within 90 days, but the NOCS, 63.7540(a)(9)(iv), and 63.7550(h) require submitting this information within 60 days. Which is correct? Or, is 63.7515(g) referring to something different? 5. 63.7521 states that Gaseous and liquid fuels are exempt from (c) and (d) which is the fuel sampling. Does this mean they have to develop a sampling plan, even though they don't have to sample? 6. Are sources not subject to an emission limit required to submit a Notification of Compliance Status? 63.7545(e) says if 63.7530(a) applies then they need to submit the NOCS. But, sources not subject to an emission limit aren't subject to 63.7540(a). If they don't have to submit an NOCS, then does 63.7530(e) apply? 7. 63.7555(d) says it only applies to those subject to emission limits, but (d)(3) is a requirement for limited use units to keep records of hours of operation. Does this apply to them despite what the first sentence of 63.7555(d) says? Do other requirements in that section apply to sources not subject to emission limits? If so, which ones? 8. For units less than 10 MMBtu/hr: do the other gas 1 units have to do any of the fuel analysis since the requirements are the same regardless of what fuel they are burning? 63.7521 (f-i) What about the notifications in 63.7545(f) and (h) - do those apply to units that are < 10 MMBtu/hr? 1. Heat input capacity: is this the design capacity of the unit the unit nameplate listing the rated heat input capacity on the unit? I assumed it is, but wanted to check. What does this statement mean?: "The act of entering into a contractual agreement with a supplier of natural gas established for curtailment purposes does not constitute a reason that is under the control of a facility for the purposes of this definition." It is in the definition of period of gas curtailment, but it doesn't make much sense to me.
2011-04-08 | Northern Natural Gas | NESHAP 4Z | Mark Smith | Region 7 | Northern Natural Gas is requesting a determination in regards to 40 CFR 63.6625 (h), which states “If you operate a new, reconstructed, or existing stationary engine, you must minimize the engine’s time spent at idle during startup and minimize the engine’s startup time to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the emission standards applicable to all times other than startupin Tables 1a, 2a, 2c, and 2d to this subpart apply.” Per the above paragraphs, to comply with 63.6625 (h) the equipment, including the catalyst must be at steady state within 30 minutes of initiating engine startup; therefore the catalytic inlet temperature must be at or above the minimum catalytic inlet temperature required in Tables 1b and 2b of this subpart, otherwise it is a deviation that must be reported per 63.6650. There may be circumstances outside of normal operation (i.e. low ambient temperature) in which the minimum catalytic inlet temperature cannot be met within the required 30 minutes of initiating engine startup and the engine is shutdown within 30 minutes of initiating startup to avoid a deviation of 63.6625 (h). Are there any restrictions on initiating another startup of the engine and/or the time frame to complete the subsequent startup? | In consultation with EPA Office of Air Quality Planning and Standards (OAQPS), Office of General Counsel (OGC) , and Office of Compliance (OC), EPA reads the 30 minute limit for engine startup as referenced in Tables 1a, 2a, 2c, 2d, and 40 C.F.R. §63.6625 (h) to not exclude startup operations beyond the 30 minute limit. Instead, the 30 minutes of startup is a period when the numerical emission limitations under normal operation do not apply. For example, an existing non-emergency, non-black start 2 stroke lean burn (SLB) stationary RICE greater than or equal to100 horsepower (HP) but less than 500 HP at a major source for HAPs, must limit concentration of carbon monoxide (CO) in the stationary RICE exhaust to 225 parts per million, volumetric dry (ppmvd) or less at 15 percent oxygen (O2). During startup, the 2SLB engine does not have to limit CO exhaust to 225 ppmvd. After 30 minutes of engine startup, the standard applies and compliance is determined over the course of 3-hour block averages of all recorded readings. See 40 C.F.R. §63.6625
2011-04-07 | Bob & Sarah | NESHAP 6J | Melissa Ellis | NDEQ | Are boilers that burn natural gas still affected sources under 6J (like engines - subject but no requirements apply)? | You can state that they aren't subject to the rule. It isn't like the engines where the rule says all engines are subject then lists caveats to who has requirements. The boiler rules don't list natural gas boilers as "affected sources" and states that gas-fired boilers aren't subject. The only affected sources are those within a subcategory (oil, coal, biomass).
2011-04-06 | Melissa E. | NESHAP 5D & 6J | Jon Knodel & Brian Shrager | Region 7 and OAQPS | Are boilers used to generate electricity for the grid subject to these rules? My thought is they would fall into the "institutional" category. However, the definitions of commercial, industrial, and institutional in the rule are pretty vague. We have a few municipalities that have boilers less than 25 MW that supply electricity to the grid. | Jon: The final rules under Subparts DDDDD and JJJJJJ [National Emission Standards for Hazardous Air Pollutants for Industrial, Commercial, and Institutional Boilers Area Sources] define an industrial boiler as "a boiler used in manufacturing, processing, mining, and refining or any other industry to provide steam, hot water, and/or electricity." So, I think the less-than-25-MW electric generating units you are looking at would be classified industrial boilers under either the major- or area-source MACTs, depending on the amount of HAPs from the facility. Me: Each of the definitions for "commercial, industrial, and institutional" in 6J include "provide steam, hot water, and/or electricity." Would a municipality still be considered "industrial?" To me, it seems to fit into "institutional" more than industrial? What are your thoughts? Also, I just noticed that the definitions in 5D do NOT include "to provide electricity." I know we have some large boilers less than 25 MW at EGU's that are operated by municipalities. I'm afraid they wouldn't be subject, but I don't think that was the intent. Thoughts? Jon: Iowa raised the same question this morning which we referred to Brian Shrager at OAQPS. I believe such units are still classified as "industrial boilers", but will confirm for sure when we hear back.Brian Shrager, OAQPS: The 13 and 15 MW units are industrial boilers. They still produce steam, and whether the steam is used for electricity generation or any other use, a unit is still considered a boiler.
2011-04-06 | Melissa E. | NESHAP 5U | Lisa Hanlon | Region 7 | I have a question regarding the applicability in Table 10 of the EGU MACT. It states there are two categories for coal-fired units. One is for existing units designed for > 8,300 Btu/lb and the other is for < 8,300 Btu/lb. However, when you read the narrative in the previous pages it talks about units that “burns any virgin coal in an EGU designed to burn ……” Our boiler is designed to burn coal less than 8,300Btu/lb (our coal contract specifies not less than 8,200) but we typically burn coal above 8,300 Btu/lb. Is the categorization based on what is actually combusted or design capacity? EPA also mentions the furnace height-to depth ratio as a deciding factor. Looking solely at that parameter our furnace would be greater than 3.82 and fall into the second sub-category. It is not clear to me that PGS boiler one can fully meet the requirements of either sub-category but I am assuming the best fit would be sub-category 2. | Me: My interpretation would be that it would apply to what the unit is designed to burn. In your case, it is designed to burn coal less than 8,300 btu/lb and would follow those guidelines. I think if you are planning to submit comments, it would be a good idea to bring it up. It doesn't make much sense how it is currently written. I can run it passed EPA if you'd like to get their initial thoughts, too. Marty Stange, Hastings Utilities: WEC1 is in the same condition as PGS. I suspect other plants have the same question. We would appreciate hearing what EPA has to say on the definition that would apply. EPA:
2011-04-06 | Bob Sheeder | NESHAP 6J | Melissa Ellis | NDEQ | Is a boiler using oil as a backup subject to 6J? | If the source ONLY plans to burn the diesel during periods of curtailment or supply emergency, then they wouldn't have to comply with the rule. They are allowed to burn it up to 48 hours for testing per year. If they decided to burn it and it didn't meet the curtailment definition (see below) and it wasn't for testing, they would have to comply with the rule immediately. Oil subcategory includes any boiler that burns any liquid fuel and is not in either the biomass or coal subcategories. Gas-fired boilers that burn liquid fuel during periods of gas curtailment, gas supply emergencies, or for periodic testing not to exceed 48 hours during any calendar year are not included in this definition. Period of natural gas curtailment or supply interruption means a period of time during which the supply of natural gas to an affected facility is halted for reasons beyond the control of the facility. The act of entering into a contractual agreement with a supplier of natural gas established for curtailment purposes does not constitute a reason that is under the control of a facility for the purposes of this definition. An increase in the cost or unit price of natural gas does not constitute a period of natural gas curtailment or supply interruption.
2011-04-04 | Gary Bergstrom - LLCHD | NESHAP 4Z | Clark Smith |  | We’re currently working though a permit application for a portable concrete crushing plant. The plant utilizes the same diesel engine to provide power to crush concrete, and also to provide power for propelling the crusher. Subpart ZZZZ applies to ‘stationary reciprocating internal combustion engines’, defined as follows: “Stationary reciprocating internal combustion engine (RICE) means any reciprocating internal combustion engine which uses reciprocating motion to convert heat energy into mechanical work and which is not mobile. Stationary RICE differ from mobile RICE in that a stationary RICE is not a non-road engine as defined at 40 CFR 1068.30, and is not used to propel a motor vehicle or a vehicle used solely for competition.” Of course, the progression leads to the definition of a non-road engine in Part 1068. In Section 1068.30, the definition of a non-road engine is an internal combustion engine that meets any of 3 criteria. The criteria that most clearly applies to a concrete crusher like this would appear to be (1)(i), which states, “It is (or will be) used in or on a piece of equipment that is self-propelled or serves a dual purpose by both propelling itself and performing another function (such as garden tractors, off-highway mobile cranes and bulldozers).” However, criteria (1)(iii) appears to loosely apply, as well. It states, “By itself or in or on a piece of equipment, it is portable or transportable, meaning designed to be and capable of being carried or moved from one location to another. Indicia of transportability include, but are not limited to, wheels, skids, carrying handles, dolly, trailer, or platform.” Under the definition of what is not a non-road engine, criteria (2)(iii) states that engines covered by criteria (1)(iii) are no longer considered non-road engines if they remain at a location for more than 12 consecutive months (or a shorter period of time for seasonal sources). Now, one could make the argument that anything included in criteria (1)(i) and (1)(ii) could also be covered by (1)(iii). For example, a bulldozer is clearly covered by (1)(i)…but it could also be covered by (1)(iii), because it is in a piece of equipment, and it is capable of being carried/moved from one location to another. This would lead to the conclusion that, if a bulldozer is operated a one location for more than a year, it is no longer a non-road engine, and is regulated by the RICE MACT. Doug Tangeman, who is our primary contact for air toxics rules, and I have been discussing the matter, and it seems to us that criteria (1)(iii) of the non-road definition exists to include engines that are not otherwise included in criteria (1)(i) and (1)(ii)…and that because a self-propelled concrete crusher best fits in criteria (1)(i), the applicability criteria (1)(iii) is immaterial. And because criteria (2)(iii) only applies to engines otherwise included in (1)(iii), it does not matter how long a crusher of this type is operated in one location. The conclusion that this has led us to is that concrete crusher engines that are used both for propulsion and for process power are considered non-road engines, regardless of the duration of operation in one location, and are not covered by Subpart ZZZZ. | I agree with your assessment. Since the exclusion in 2(iii) refers back to 1(iii), it would only apply to that section and would not apply to sections 1(i) and 1(ii) of the definition. We consider everything meeting the criteria in sections 1(i) and 1(ii) of the definition to be nonroad and therefore not regulated as a stationary source. To assist you with nonroad engines, I will be sending you a copy of two draft applicability determinations we are working on (a couple of format issue to finalize). While draft, we are very confident these will be our final determinations.
2011-03-28 | Tim Plander - Olsson Associates | NESHAP 6X | Joe Terriquez |  | I have a question for you on NESHAP Subpart XXXXXX. In 40 CFR 63.11516 (f), if 2000 pounds or more of welding rod are used in a year, then a facility is required to perform visual observations of welding fume. I am assuming the visual observation requirements do not apply if a facility only uses welding wire. Please confirm. Welding wire is stored in a coil. Welding rod is stored as distinct metal pieces. | I talked with Joe Terriquez at EPA Region 7 about the wire vs. rod question. Joe said that it applies to both wire and rod. So that is the way I am going to go about it unless I hear otherwise.
2011-03-15 | Melissa E. | NESHAP 4F | Hugh McCullough | 'McCullough.Hugh@epamail.epa.gov' | I have a question on MON. My memory is telling me that an existing source that adds another MCPU would still be classified as existing unless: the added MCPU was major by itself or if it adding the new unit meets the definition of reconstruction. I also found the following on the Tennessee website: "New sources are created by reconstructing existing sources, constructing new greenfield facilities, or constructing an addition to an existing source that is a dedicated MCPU and has the potential to exceed 10 tons per year of an individual HAP or 25 tons per year of combined HAP. Reconfiguration of existing equipment does not constitute construction." Is this correct? Further, If the added MCPU IS major or does meet reconstruction, would the whole facility be classified as "new" or would they have to comply with new source requirements for one MCPU and existing for the other MCPU? | I think you are correct. I was thinking that there might be a possibility for the "Family of Materials" definition to come into play, but I don't think it does in this instance.
2011-03-10 | Melissa E. | NESHAP 5D | Clark Smith |  | For boilers to take a limit of <876/yr to meet "limited use," does the limit have to be in a construction permit or can it be in an operating permit? | It can be in either. Preferrably OP if a CP isn't open already. They don't have to fill out all of the forms, only the general information and a description of the limit they want to take and why.
2011-03-10 | Melissa E. | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov | Page 12864 of the preamble, last sentence at the bottom of column 2, says that a CPMS plan must develop and submit for approval a site-specific monitoring plan for the CPMS. I don't see anywhere in the amendments or in the 8/20/10 rule where it says they have to submit the plan for approval. Do you see it somewhere in the regulatory text? •    63.6625(b) states "For an affected source that is complying with the emission limitations and operating limitations on 3/9/11, the requirements in paragraph (b) of this section are applicable 9/6/11." My assessment is this extended compliance period for the CPMS is only applicable to the following engines whose compliance dates were before 2010: 4SLB > 250 HP < 500 @ Major; 4SRB > 500 HP @ major; and New CI, 4SLB, 2SLB > 500 HP @ major. Is that right? | Looking at Page 12864, I do not see the requirement to submit the plan for approval in the 8/10/2010 rule. I looked through the rule FR notice and didn't see it there either, so I'll admit I'm a little confused on that one. For 63.6625 (b) that is how I've read it as well. This should only affect the engines where their compliance date was before 2010 and the CPMS provisions took effect when the August 2010 came out. As more questions come in, I'll make a single list to shoot up to Melanie.
2011-03-01 | Melissa E. | NESHAP 6B & 6C | Clark Conklin | Clark Conklin, Chief Deputy Fuels Safety Division Nebraska State Fire Marshal (402) 471-9467 clark.conklin@nebraska.gov | As you may know, EPA has finalized a regulation for gasoline dispensing and distribution stations. I had one of the inspectors ask how we know whether they are complying with the submerged fill requirements. I'm not very familiar with gas stations, cargo tanks, etc. Can you help me shed light on this? Since it is a State regulation for underground storage tanks to use submerged fill, I thought you would know. | Well…I’m not exactly sure where to start…visual inspection can be done easily, if you know what you’re looking for. It’s a little difficult to explain but you know it when you see it (paraphrasing the Supreme Court). In order to comply with submerged filling, underground tanks must be equipped with a fill tube that extends to within 6 inches of the tank bottom. This can be easily determined by removing the fill cap and looking down to see if this fill tube is visible and in place. You should be able to see the liquid level contained within this tube, usually aluminum. In some cases a “coaxial” fill port is necessary but I’m not exactly sure what those look like since our rule doesn’t require this device. In addition, filling of underground tanks must be done through a liquid-tight connection to the UST fill tube. Some aboveground tanks may be equipped with the same feature, but more than likely larger tanks would have a fill pipe that is permanently connected to the top of the tank and visual observation could not be made. Installation drawing/documents should indicate the presence of the fill tube extension. Many vertical ASTs at bulk plants fill from the bottom through a permanent, dedicated pipe and this procedure would be considered submerged filling. When filling tank vehicles at a bulk plant, the vehicles are filled through the top, through open lids (domes) or filled through the bottom through piping attached to the bottom of each compartment of the vehicle. Top filling tank vehicles should be completed with a large nozzle with a long “spout” that will extend to within 6 inches of the bottom of each compartment. These devices are located at the “loading rack” at the bulk plant. Bottom filling vehicles is completed with tight filling connections much the same as bottom filling tanks occur. However, this is a little more technically complicated as there must be a metering system involved so that the tank compartment is not overfilled. I know you asked about underground tanks at service stations but I didn’t want to forget about other types of systems you all may encounter. If you’d like more information contact me. Maybe we would be able to arrange a real life tank exhibit at an actual service station/convenience store, showing one of these devices in place (or not as the case may be).
2011-02-28 | Melissa E. | NESHAP 6B & 6C | Bill Peterson | peterson.bill@epamail.epa.gov | 1. How do we know they are complying with the submerged fill requirements? We obviously can't measure inside the tank. I'm sure there is an industry standard, but I'm not sure what that is. 2. For 6B - I know the 20,000 gallons/day throughput for determining if you are a bulk plant or bulk terminal is based on maximum design capacity. Is it the same for the tank and loading rack thresholds (480 gallons/day and 250,000 gallons/day)? Is it how much the maximum throughput would be loading into plus loading out of the tank or rack? 3. Gasoline definition - I found information indicating that E85 would still have a vapor pressure above 4 psi (27 kp). Do you know if anything above E85 would still be considered 'gasoline?' 4. For 6C - I just want to clarify that loading gasoline into the fuel tank of a stationary engine (i.e. generator) would not fall under 6C. Is that right? | 1. How do we know they are complying with the submerged fill requirements? We obviously can't measure inside the tank. I'm sure there is an industry standard, but I'm not sure what that is. I don't know if there is an industry standard. I have heard that some inspectors simply use a pipe with a bolt attached to one end. They run the pipe through the fill pipe until it hit the bottom of the tank. They slide the pipe over and lift up. The bolt catches the bottom of the submerged fill pipe. As a result, they determine distance from the submerged fill pipe is from the bottom. 2. For 6B - I know the 20,000 gallons/day throughput for determining if you are a bulk plant or bulk terminal is based on maximum design capacity. Is it the same for the tank and loading rack thresholds (480 gallons/day and 250,000 gallons/day)? Is it how much the maximum throughput would be loading into plus loading out of the tank or rack? Table-1 and 2 as revised in the January 24, 2011 Federal Register states that the gasoline through put of 480/250,000 gallons per day is calculated by summing the current day's throughput, plus the throughput for the previous 364 days and then divide by 365. So this is an actual through put as opposed to a maximum design calculation. The preamble language on page 4166 talks about choosing either the volume loaded or dispensed (loaded out of) in calculation the throughput. You would not do both (loaded plus dispensed from) because that would be double counting. 3. Gasoline definition - I found information indicating that E85 would still have a vapor pressure above 4 psi (27 kp). Do you know if anything above E85 would still be considered 'gasoline?' Page 4173 of the January 24, 2011 Federal Register has a discussion that denatured ethanol (i.e. containing about 5% gasoline) does not meet the definition of gasoline. 4. For 6C - I just want to clarify that loading gasoline into the fuel tank of a stationary engine (i.e. generator) would not fall under 6C. Is that right? Based on the discussion in the preamble of the January 24, 2011 Federal Register (see page 4157) and even the revised definition of Gasoline Dispensing Facility (which includes generators), generators would fall under 6C. Is there preamble or regulatory language that you read which suggests otherwise?
2011-02-03 | Melissa E. through Eric Sturm | NESHAP 4Z | Melanie King | King.Melanie@epamail.epa.gov | Nebraska came across an interesting situation while trying to determine whether an engine should be considered "new" or "existing" under the RICE MACT. An engine was previously used at a facility (for a period less than 12 months). Then it was sold back to a distributor before proposal date of the MACT. The same engine was then bought by a new company after proposal date of the MACT. Reconstruction has not occurred on the engine. The issue being, would this engine be considered "existing" under the MACT given 63.6590 (a)(1)(iv) "A change in ownership of an existing stationary RICE does not make that stationary RICE a new or reconstructed stationary RICE"? Keep in mind that there might not be any way of knowing how the engine was used at the previous facility. If it was used as a non-road mobile engine at the previous facility, would it be considered "new" today? Does its use matter? | As long as it was used anywhere prior to the applicable existing/new cutoff date (12/19/02 or 6/12/06 depending on the size and major/area source status), it would be an existing engine, even if it was used as a nonroad engine at the time, or it was owned by someone else. This question has come up a few times recently and we've said that for subpart ZZZZ the date of construction would be the date it was first installed anywhere when it was a brand new engine, even if it was a nonroad engine at the time.
2011-02-03 | LLCHD | NESHAP 6H | Doug Tangeman | dtangeman@lincoln.ne.gov | I’ve also had a couple issues arise during my inspections regarding compliance status of spray guns. First is the issue of the compliance status of facilities that not only do auto body painting, but also apply spray coatings that use specialized guns (such as spray guns used to apply truck bed liners or undercoating/rock chip protection coatings). The guns are not HVLP or equivalent and are specialized to apply the specific coating. The 2nd issue that’s come up regularly is what to do about guns that have been discontinued or cannot be identified (so documentation can’t be tracked down) but the gun is marked “HVLP”. I was also going to ask 1. If your agency has been out doing any inspections for 6H and 2. If yes, what issues have the inspectors run into? As of right now, I’ve been to about half of the identified sources here in Lancaster County (roughly 35) and I’d be interested to hear what other agencies have been finding. Thanks. | We have processed/approved all exemptions requested (approximately 20). So, I'm not sure where that information came from. The truck bed and undercoating guns may be airless or air assisted airless. Guns do not have to be HVLP only. See 63.1173(e)(3). In talking to some auto body guys, they said the undercoating guns would be considered air assisted airless and that would comply under the rule. As far as HVLP guns that have no record, they need to find something on the internet or get something from a gun supplier. There should be some information available. I'm guessing if they say there isn't information available, they aren't compliant. Even if a gun is discontinued, they should still be able to get information from the manufacturer. We have not been doing inspections and won't unless we have a complaint. Since we aren't collecting fees like you guys are, we don't have the money to do routine inspections. I'm guessing we will start getting complaints from other shops that are complying against shops that aren't. So, I don't have anything to tell you. What have you been finding?
2011-02-03 | LLCHD | NESHAP 6H | Doug Tangeman | dtangeman@lincoln.ne.gov | That’s what I thought about the exemptions. I’m willing to bet the information came from some upset shop owners. The two people who called me to ask about it said that they’d heard the reason NDEQ wasn’t doing the exemption was because “they want their money from the shops”. I knew you guys weren’t collecting fees for 6H and told them that particular reason didn’t make sense (among many other reasons). But I said I’d follow up with you to make sure (the rumor mill is alive and well the auto body business it seems). As far as those specialty guns go; from what I’ve seen, they aren’t airless or air-assisted airless (or electro deposition, etc). For instance, with the truck bed liners, I’ve seen two shops that have a liner system where the “coating” is a two-part system where the gun is specifically made to be hooked up to two siphon hoses (which are hooked up to drums containing the “A” and “B” parts of the liner) and an air hose. The two parts are drawn into the gun, mixed , and then atomized and sprayed onto the vehicle (where the resin then hardens). The spray gun is specifically made to spray that two-part system, you can’t spray anything else with it. It’s also not a system where you could hook up a regular paint gun either. But it still means all of the definitions (“coatings” “spray-applied coating operations”, etc). And we can’t issue them an exemption either because even though the bed liner coatings don’t have target HAP, their facility also does regular auto body painting as well and some of their toners have target HAP. The issue of not being able to find documentation comes up often because not all spray guns have markings. I’ve run into several shops that have guns that are marked “HVLP” but don’t have anything else identifying a make or model. What I’ve been telling these shops is that they need to either a. only use these guns with a 3 oz cup or b. take it out of the shop. Quite a few shop owners aren’t too happy about this because the gun IS marked “HVLP”. Did you have any thoughts on this? As far as other things I’ve found go, I found that most of the shops (about 70%) do not have all of the documentation and paperwork that the rule requires them to keep. Most have air filter efficiency documentation and painter training certificates, but over half do not have copies of their notifications and most do not have documentation for all of their spray guns. There have been a couple shops that have constructed spray booths that are ventilated at positive pressure instead of negative pressure. I have also found that many shop owners/operators are not aware that they cannot do priming in their shop (most of these shops are also not aware of the exception for 3 oz paint cups either). I think they misunderstood the rule does not regulate just “painting” but rather all “spray coating” of vehicles. The other large issue that I get asked by almost every body shop owner is what we are doing about the ‘underground’ guys. So far I’m just getting names and addresses to follow up with, but it looks like the amount of people/places that routinely do spray coating of vehicles somewhat ‘off the grid’ number about as many as the legitimate body shops. I’ve done 32 inspections and have a list of 25 places to follow up with already. I’ve also been in contact with the paint suppliers and I’ve been told only about 50% of their paint sales is from the body shops. | I talked to Joe Terriquez from EPA Region VII a bit about some of your questions. It sounds like the truck bed lining system is using an air-assisted airless. We could be wrong since we didn't see your system. Maybe you can talk to him a bit more about it, but your description seemed to fit air-assisted airless. He agreed with me that they should have some sort of documentation for the HVLP. The manufacturer will have something even if the gun is discontinued. He also said most likely anything with a raised HVLP stamp is legitimate, but if it is stamped in and not raised, it might not be (if you can't find paper work). The spray booths that are vented at positive pressure, are they automatic pressure balancing system booths? If so, positive is o.k. I'm sure you found this out, but thought I'd ask just in case.
2011-02-03 | Bob Sheeder | NESHAP 4Z | Melissa Ellis | NDEQ | I have a question regarding the emergency vs. non-emergency distinction in NESHAP 4Z. I am working on a permit for the Wahoo Municipal Power Plant, and I need to clear this question up before the reviewer will sign off on the review of the permit. This facility has two engines greater than 500 HP that they are treating as emergency engines. I have written the permit to say that the engines can be treated as emergency engines, but if at any time they are not operated in accordance with 63.6640(f)(1), the engines become subject to all requirements of all non-emergency engines. My interpretation of the rule is that if an engine is designated as an emergency engine, but then is not operated in accordance with 63.6640(f)(1), the engine becomes non-emergency and can no longer be considered an emergency engine at any point in time. The reviewer believes that an engine under 4Z can switch between non-emergency and emergency status at any time and as many times as they like during the permit term. Can you shed some light on this for me? I looked at the Air Toxics Notebook, but couldn't find where this question has been addressed by anyone. Thanks for your help. | An engine can go between emergency and non-emergency, but they would have to comply with non-emergency right away. So, it wouldn’t make sense for them to go back and forth. They would already have to put the controls on and do testing. They could go back to operating as emergency at some point and would have to prove it as such. I guess it would get them out of testing every 3-5 years. Your interpretation is correct and as 63.6640(f)(1) states: If you do not operate the engine according to the requirements in paragraphs (f)(1)(i) through (iii) of this section, the engine will not be considered an emergency engine under this subpart and will need to meet all requirements for non-emergency engines. I'm not sure what the reviewer is concerned with. If you want to have them talk to me about it, I'm fine with that.
2011-02-03 | Sarah Starostka | NESHAP 4Z | Melissa Ellis | NDEQ | I have a existing black-start engine 525 HP at a major source. I looked through the ZZZZ guidance, but did not see anything specifically regarding black start engines at a major source. Would this mean that there are no specific requirements at this time for the engine? | For major sources, there are specific requirements for black start that are the same as emergency for engines less than 500 HP. If it is >500 HP at major, the black start engine would probably qualify as a limited use engine. If that is the case, they wouldn't have to do anything if they were existing. If they are new, they may have to comply with NSPS.
2010-12-22 | LLCHD | NESHAP 6H | Melissa Ellis through Joe Terriquez | 913-551-7105 | I had one of the local auto body suppliers give me a call yesterday afternoon asking for some guidance for his customers. His question was how we were going to handle what he termed the "el cheapo" guns from international manufacturers that have "HVLP" stamped on them, but for which they (the manufacturer) won't provide any documentation that they are indeed HVLP. In one particular case he mentioned a particular gun was stamped "HVLP" but the manufacturer told him that they made so few of the gun that it wasn't worth the money to get it tested. I said we would required the information from the manufacturer. What are your thoughts? | I would agree with your statement, I would hope that these are not new products that are trying to take the rule literally with the HVLP stamp.
2010-12-22 | Melissa Ellis | NESHAP 6H | Melissa Ellis through Joe Terriquez | 913-551-7105 Terriquez.Joe@epamail.epa.gov | An auto body shop receives the exemption approval and they later take on a special job requiring paints with the metal HAPs above the .1% & 1%. I've told them they have to comply with the rule immediately upon using the metal HAPs. Is this correct that they have to comply immediately? Also, can they receive another petition for exemption and keep going back & forth? My thought is they should only receive the petition once & if they use the metals & have to comply they wouldn't be able to get another exemption. What are your thoughts? | Yes they would have to submit notification that they are no longer going to be exempt. Unfortunately there seems to be the ability to go back and forth ( I will check with Leslye when she gets back about the once in always in), so they could file for exemption again. I would strongly discourage this practice as they will have to wait until the notifications get processed. Me: I know the rule doesn't say they can't go back and forth, but I'm discouraging it. If it comes up, we'll probably have to allow them to go back and forth, but this would be a compliance nightmare! Joe: I agree, but I think that the time that is takes to process the exemptions will probably discourage many from doing the back and forth.
2010-12-17 | OAQC | NESHAP 6H | Melissa Ellis through Joe Terriquez | 913-551-7105 | I just wanted to revisit something that was brought up in Tuesday’s training session. In the session on 6H, unless I misunderstood, you said that shops who applied undercoating with non-atomizing paint guns were required to use paint booths to do so as part of the rule since that was still a spray-applied coating. However, as I read the rule, the definition of spray-applied coatings are, “coatings that are applied using a hand-held device that creates an atomized mist of coating and deposits the coating on a substrate.” Under this definition, undercoating application using a non-atomizing paint gun would not be covered, and would thus not be subject to the rule requirements, including application within a paint booth. | I talked to Joe Terriquez from Region VII. He & Leslye Werner both agree that even though an air-assisted airless gun doesn't technically atomize the undercoating, it is still considered spray-applied & would have to be performed in a compliant booth. That is, if they are using a gun with > 3.0 oz. It seems as if these are gravity fed, so they wouldn't have a paint cup. So, even under coatings must be applied in a compliant booth. They also referenced this discussion in the preamble of the rule. Leslye & Joe said this was much like the truck bed liner discussion.
2010-12-15 | LLCHD | NESHAP 4M | Dave Salman | EPA | Definition of High Performance Coatings - references AAMA specs | High performance architectural coating in MMMM means coatings that meet particular AAMA specifications. These specifications are for decorative coatings for architectural aluminum extrusions and panels. The table at http://www.aluminum-rails.com/finishes/aama.htm shows the characteristics addressed in these specifications. Contact adhesives are not decorative coatings. The referenced specs don't have any applicability to contact adhesives. Contact adhesives are not high performance architectural coatings in MMMM. Note the citation of the spec in the def'n of high performance architectural coatings is faulty. There is no 605.2-2000. The intended specifications are AAMA 2604-02 and AAMA 2605-02. The correct citations are in the final BID which can be found at http://www.epa.gov/ttn/atw/misc/mmmm_bid_082003.pdf See page 73 (page 78 of 178 of the pdf file). More info at http://archrecord.construction.com/resources/conteduc/archives/0204Performance-1.asp http://www.arkema-inc.com/pdf/techpoly/aama_2605.pdf
2010-12-13 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | I have a question related to 4Z - Table 2b. For the catalyst pressure drop: it says maintain pressure drop across the catalyst so it doesn't change by more than 2 inches of water at 100% load plus or minus 10% from the pressure drop measured during the initial performance test. Does this mean if the pressure drop measured during the test is 10. The range is + or - 2 inches (8 - 12 inches) PLUS another 10% (.1) making the acceptable range 7.9 - 12.1? Or is the 10% representative of the load? So, it can be at 90% - 110% of load during test? Then the acceptable range is 8-12 inches? What is the 10% referring to? | The response to comments (in 2004 & 2010) suggests your second reading is what the rule writers had in mind, 100% load +/- 10%. My reading would be the same.
2010-10-14 | StoreKraft - Gary Kumpf | NESHAP Once-In-Always-In | Clark Smith - NDEQ |  | I work for Store Kraft in Beatrice and we have a Class 1 air permit. We had an inspection by Dave Brown a month or so ago for our Air Emission Inventory. The last line of his report stated we were correctly classified as a Class 1 source. I asked him if we were classified correctly by a 'once in always in' rule or if we were actually over a threshold. He told me he was not sure but did not think we would need to be a Class 1 source anymore. He was not aware of a 'once in always in' rule that would require us to stay a Class 1 source. He suggested I contact you. I was told when I took over Environmental duties that there was a 'once in always in' rule and I know Melissa has mentioned it. Maybe that is for a different source like an incinerator? Can you tell me if there is any way we can stop being a Class 1 source? There are of course a lot of requirements that cost a lot of money so if it is possible we would like to know. | The 'once-in-always-in' policy is a little confusing for the operating permit program. The policy only applies to the hazardous air pollutant (HAP) program (does not apply to criteria pollutants), and then it only applies if the source is major on the compliance date for the standard. When this happens, the source is always subject to the standard even if they subsequently reduce their HAP emissions to below the major source thresholds. The standards themselves require subject sources to obtain a Class I (major source) permit. To let you know, this is a National policy established by the EPA. Store Kraft is in this situation. The following is the discussion of this issue in the Fact Sheet for Store Kraft's Class I permit: SK is considered an affected facility under Title 129, Chapter 28, Section 001.08, which adopts by reference Title 40 CFR Part 63, Subpart JJ, “National Emission Standards for Wood Furniture Manufacturing Operations". The facility is subject to Subpart JJ because it was a major source for HAPs on the initial compliance date and falls under the definition of wood furniture manufacturer. If potential emissions are equal to or greater than 10 tpy of any single HAP or 25 tpy of any combination of HAPs the source is considered major in accordance with 40 CFR 63, Subpart A. SK also had to obtain a Class I operating permit in 2003 because it was a major source of HAPs on the initial compliance date of Subpart JJ. The NDEQ has been consistent in its application of this policy. In other words, Store Kraft is not the only source that has had to get a Class I permit due to this policy.
2010-10-05 | Melissa Ellis | NESHAP 4Z | Eric Sturm R7 & Melanie King - OAQPS | Sturm.Eric@epamail.epa.gov 913.551.7377 | • 63.6590(c)(6) states new/reconstructed emergency engines < 500 HP at a major source only have to comply with NSPS. However, in looking at the requirements for a new/reconstructed 4SLB > 250 HP < 500 HP at a major source, 63.6625(d) states new/reconstructed 4SLB emergency engines > 250 HP < 500 HP at a major source need to install a non-resettable hour meter. My question is, are these emergency engines subject to 4Z or not? If so, what are their requirements? • What are the subsequent testing requirements for existing compression ignition > 500 HP at a major source? Table 3 line 3 states stationary RICE with HP >500 located at major sources… conduct semiannual tests. However, lines 4 and 5 of Table 3 state existing non-emergency CI > 500 HP conduct testing every 8760 hours or every 3 or 5 years depending on if they are limited use. Which would it be? | Eric: • First Bullet, while the NESHAP tried to make all the standards the same for engines less than 500 hp as they are in the NSPS, they are not the same for all engines under 500 hp. EPA fully intends for sources that don't have the same standards under NSPS and NESHAP to have two sets of requirements. See response to comments below from 2007 below. In short, the engines you refer to are subject to 4Z.• Second Bullet, lines 4 and 5 of Table 3 are referring to engines > 500 hp at area sources. While it's not explicitly stated (or intuitive) that's the way I read it since > 500 hp at major sources is previously discussed in line 3. I've asked Melanie about this before, and she had the same reading. Melissa: I'm still confused on the first bullet. My question was more specific in that I was asking about emergency 4SLB >250 and <500 HP. New emergency engines <500 HP are not subject to any requirements. This would still be an emergency engine, but is also a 4SLB. So, which trumps the other? The requirements are confusing, but 63.6625(d) makes it seem like even though they are emergency and less than 500 HP, they are still subject. Eric: Emergency engines that are 4SLB >250 and < 500 hp are subject to 4Z. 63.6590 (c) further reiterates that 4SLB < 250 hp meet this standard by meeting the NSPS. Meaning that 4SLB > 250 hp have requirements under 4Z that are not in the NSPS. 63.6625 (d) is one of those requirements. Melissa:Do any NESHAP requirements apply to 4SLB >250 and < 500 hp manufactured before 1/1/08? It says the emission limits only apply to those manufactured on or after 1/1/08. How about the emergency 4SLB >250 and < 500 hp - if they are manufactured before 1/1/08, do they still have to install an hour meter? My thought is that nothing applies to the engines manufactured before, but I could be wrong! •    Existing compression Ignition > 500 HP at major source - you said they would have to subsequent testing semiannually in accordance with Table 3 line 3, but after looking at it again it only applies to those reducing formaldehyde emissions. These engines are only required to reduce CO emissions. This takes us back to the testing every 8760 hours or 3-5 years (lines 4 and 5) Also, it seems as if Table 6 lines 3, 10, 11, 12, and 13 also imply that the testing every 8760 hours applies to these sources. Can you take a look again and let me know what you think? Thanks! Eric: • According to 63.6655, I think pretty much all existing emergency CI engines must install an hour meter to ensure compliance, but the rule is silent on this requirement for SI. I'm confused why SI don't and CI do even though they both have the same definition and similar operating limitations to meet. I think it would be difficult to demonstrate compliance without installing an hour meter, but I suppose you could do some sort of other documentation (Melanie - If you have anything to add, please do.) • I think you're right. Lines 4 and 5 look like they would apply for CI > 500 hp at majors for HAPs. I must have misread the question. Melissa: Do any NESHAP requirements apply to 4SLB >250 and < 500 hp manufactured before 1/1/08? It says the emission limits only apply to those manufactured on or after 1/1/08. How about the emergency 4SLB >250 and < 500 hp - if they are manufactured before 1/1/08, do they still have to install an hour meter? It seems that the emergency SI 4SLB >250 and < 500 hp manufactured after 1/1/08 would need to install the hour meter. Eric:How about the first parts of the question: Do any NESHAP requirements apply to 4SLB >250 and < 500 hp manufactured before 1/1/08? - Best Management Practices It says the emission limits only apply to those manufactured on or after 1/1/08. How about the emergency 4SLB >250 and < 500 hp - if they are manufactured before 1/1/08, do they still have to install an hour meter? - According to 63.6655, no, but programmatically you might want to consider it. Commenced construction/manufactured after 6/16/2006 and manufactured before 1/18/2008 - would be new under Part 63 4Z and predate Part 60 4J.
2010-09-22 | Melissa Ellis | NESHAP 4Z | Eric Sturm R7 & Melanie King - OAQPS | Sturm.Eric@epamail.epa.gov 913.551.7377 | More questions related to continuous compliance. What are the continuous compliance requirements (referring to Table 6) for these engines: existing non-emergency ci > 300 HP < 500 HP at area source and existing non-emergency ci >100 HP < 500 HP at major source? I may be going crazy, but I don't see them mentioned in Table 6 at all. I know they are subject to numerical limits and have to perform initial testing, but I don't know what they have to do for continuous compliance. Thanks for your help! | I don't see any requirements in Table 6 for existing non-emergency CI (or SI) less than 500 hp. Yes, some have numerical emission limitations, but I don't see any requirements to demonstrate continuous compliance in the tables. Melanie - Is this correct? If these engines do have to demonstrate continuous compliance, where should state permitters/regulators point to? Melanie: They would have to point to the general duty to minimize language in 63.6605. Eric: Would that be true for all compliance requirements not explicitly listed in the tables? Melissa: When all the other engines are listed in Table 6 except for those, it implies there are no requirements to demonstrate continuous compliance. Do they have to monitor temperature, pressure drop, anything? Or is a one time test their only compliance requirement? Thanks for your help with this! Melanie: They just have the one-time test and then the general duty to minimize requirements (63.6605(b)).
2010-09-20 | NNG - Scott Ammon | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | if an existing 4SRB engine greater than 500 hp at a major source of HAP is reconstructed, would the reconstructed engine be subject to both the RICE MACT and the NSPS? There would be 2 different emission standards to comply with. NSPS JJJJ | Eric Sturm response: I read it the same way. In the initially proposed RICE MACTs, I think they addressed this situation better where if you had a reconstructed engine, then you were suppose to comply with the NSPS emission standard at that time. It seems there are conflicting standards now, and I'm not sure why. But, compliance with NSPS should be sufficient for compliance with the NESHAP. You'll need to work with your permitting agency make sure they see it the same way. Let me apologize for misleading you in my first response. EPA addressed this issue in the Response to Comments in 2007 when the SI NSPS was proposed along with additions to the NESHAP. EPA's response clearly states that sources will have to meet emission limitations under two different standards. Although for most engines under 500 hp, the NESHAP and NSPS will be the same, in your case (>500 hp 4SRB) the standards are not the same and EPA fully intended sources to meet both obligations
2010-09-16 | Melissa Ellis | NESHAP 4Z | Melanie King - OAQPS | Phone: (919) 541-2469 king.melanie@epa.gov | For an engine not subject to numerical standards: what do they have to do to comply with 63.6635? When reading it, it seems to imply they are talking about those subject to numerical standards and not those subject to work practices. Can you confirm? I've asked Eric Sturm from R7 and he is reading as I am: that it only applies to those with numerical standards. But, we thought it would be a good idea to hear it from you. It is another one of those sections that is pretty vague. | That is correct that nothing in 63.6635 would apply to engines that are subject to work practice requirements, since they are not doing any continuous monitoring to show compliance with the rule.
2010-09-13 | Melissa Ellis | NESHAP 4Z | Melanie King - OAQPS | Phone: (919) 541-2469 king.melanie@epa.gov | If I understand correctly, an existing emergency engine at an area source is not subject to the reporting requirements in Table 7. Can you tell me how 63.6640(e) applies? It refers to reporting when you don’t meet the requirements of Table 8 (general provisions). Does this requirement apply to an existing emergency engine at an area source? What type of reporting is required and when are reports due? Would sources subject to numerical standards be subject to this? Would they include the information in their semiannual compliance report? | No reporting is required for emergency engines. Sources that are subject to numerical emission standards would have to report per 63.6640 (e) and they would report that information in the semiannual (or annual if applicable) compliance reports.
2010-09-08 | Melissa Ellis | NESHAP 6C | Bill Peterson | (913) 551-7881 Peterson.Bill@epamail.epa.gov | Compliance with 6C for coaxial system disconnect. | The consultants and regulated community in Region 7 have been getting a conflicting interpretation of the regulations. The issue involves coaxial systems and the type of connection that is required on the end of the system when it is disconnected from the storage tank. The two options are 1) a "poppet valve" (or equivalent device which seals upon disconnect), and 2) a cap which fits on the end of the coaxial system. As a result, I obtained an interpretation from both OAQPS and OECA so that we are implementing the regulations consistently on a national basis. EPA Headquarter's response was that a "poppet valve" (or equivalent device which seals upon disconnect) is required by the regulations. A cap placed on the end of the coaxial system would not meet the requirements. The poppet valve is spring loaded so that when it is disconnected from the tank, it immediately closes and prevents gasoline vapors from escaping at the end of the coaxial system. Alternatively, a cap placed on the end will prevent vapors from escaping but there is a very brief period of time that elapses once the coaxial system is disconnected from the tank and when the cap can be installed. During this brief time period, vapors escape from the end of the system into the atmosphere because the pressure in the tank is usually a little above atmospheric pressure. In Table-1 of Subpart CCCCCC, under letters (a) and (b), it states: a) All vapor connections and lines on the storage tank shall be equipped with closures that seal upon disconnect. b) The vapor line from the gasoline storage tank to the gasoline cargo tank shall be vapor-tight, as defined in § 63.11132. Therefore, a poppet valve (or equivalent device which seals upon disconnect) is required the regulations. A a cap placed on the end of the coaxial system would not meet the regulatory requirements. It is my understanding that this issue only arises with coaxial system as opposed to tanks equipped with dual point systems.
2010-09-02 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | Questions from Scott Ammon of Northern Natural Gas to Eric Sturm My questions are regarding the condition “Minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the non-startup emission limitations apply.” This will be a difficult condition to comply with during the winter months. 1) For existing 4SRB RICE at a major source of HAP, what is the compliance date for this condition? 2) What needs to be recorded to demonstrate compliance with this condition? We can document that the unit was loaded within 30 minutes of initiating the start of the unit, but the minimum catalytic temperate is based on a 4-hour rolling average and not an instantaneous reading. If we demonstrated that the engine is loaded within the 30 minute time frame, does the instantaneous minimum catalytic temperature need to be above 750F within the 30 minutes as well or, can we demonstrate compliance if the unit is loaded in the 30 minute time frame and the first 4 hour rolling average reading is above 750F? Just to reiterate, an instantaneous catalytic temperature above 750F is not required by the regulation and will prove difficult to obtain in a 30 minute startup window in the winter time if required. | 1) February 26, 2007 - these were initially a part of the regulated affected source in the 2004 RICE NESHAP. However the startup requirement wasn't in place until 5/3/10, compliance with the startup provisions would be required by 5/3/13. 2) For the 30 minute start-up time limit, I don't see anything in the rule or the response to comments on how to demonstrate the engine is loaded after 30 minutes or that the proper inlet temperature is being met. In the response to comments, August 10, 2010, EPA responded on the SSM provision... "Response: EPA is also including a requirement in the final rule to minimize the engine’s time spent at idle and minimize the engine’s startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes, after which time the otherwise applicable emission standards apply. As with any work practice, CAA section 112(h)(3) and EPA’s implementing regulations at 40 CFR 63.6(g) provide that major sources can petition the Administrator for approval of an alternative work practice, which must be at least as stringent as what is required in the regulation..." Additionally, the rule has a foot note in Table 2c for the SSM provisions... "3 Sources can petition the Administrator pursuant to the requirements of 40 CFR 63.6(g) for alternative work practices." So, other than recording an instantaneous temperature reading at 30 minutes after start up, I don't know of any way to demonstrate compliance with the 30 minute SSM provision. If the catalyst inlet temperature cannot be met after 30 minutes (i.e. in the winter time, which seems completely understandable), then the source is allowed to petition EPA to extend that time.
2010-09-02 | Dan May - OAQC | NESHAP 6C | Clark Conklin, Chief Deputy Fuels Safety Division Nebraksa State Fire Marshal | (402) 471-9467 Clark.Conklin@nebraska.gov | Does the state fire marshall have regulations requiring vapor balance and submerged fill at gasoline dispensing facilities? | The upshot seems to be that, since – under Nebraska Title 159, Chapter 7, 004.01D – all USTs must have submerged fill no more than 6 inches from the bottom of the tank, all GDFs with throughput greater than 10,000 and less than 100,000 gallons are already meeting that requirement under an applicable state regulation – thus, no initial notification or notification of compliance needed for those facilities if they were already operating prior to January 10, 2008. For those facilities with greater than 100,000 gallons throughput, since there is no state regulation requiring vapor recovery/balancing systems, initial notification or notification of compliance is still required.
2010-08-25 | Clark Smith | NESHAP Once-In-Always-In | Jon Knodel & Pat Scott | Region VII | PGLA was part of Cargill Complex of sources and major due to definition under NESHAP. They were subject to Subpart FFFF and compliance date has passed. They are under different ownership and not part of the Cargill complex anymore and not major source. Are they still subject to FFFF? | PGLA-1 has been classified as a major source under the Hazardous Air Pollutant (HAP) program. As such, it has been subject to the NESHAP, Subpart FFFF, MON. Under the EPA’s once-in-always-in policy, any source that is major on the compliance date for a standard will remain subject to that standard regardless of any changes at the source. Because the compliance date for this standard has passed and PGLA-1 was major on that date, they will remain subject to the standard. Because PGLA-1 is subject to Subpart FFFF, they are then required to obtain a Class I permit under the provisions of Title 129, Chapter 5, Section 001.01C. Unless exempted in the standard, Section 001.01C requires “Any source, including an area source, subject to a standard or other requirement under Chapters 23, 27 or 28” to obtain a Class I permit. With PGLA-1 being subject to Subpart FFFF (a Chapter 28 requirement) and there being no exemptions under that standard, they must obtain a Class I permit.Prior to sending this email, I did verify the above interpretation with EPA Region 7. Staff at Region 7 stated that the once-in-always-in policy would prevail in this situation. The operations at PGLA-1 are subject to Subpart FFFF and a change in ownership does not change the applicability of this standard.
2010-08-09 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | Does an emergency RICE (with no numerical emissions limitations) at an Area source need to submit an annual Deviation Report and semi-annual COC as described in 63.6650? | Area sources not subject to numerical standards do not need to submit annual or semiannual reports per Table 7 of the rule.
2010-08-09 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | In preparation for our Board meeting next week I was hoping that you could please pass on a question to the Region VII rulewriter: How much flexibility does a generator have in designating non-emergency or emergency? For instance, if a generator considers itself an emergency unit, but future market conditions make it worthwhile to become non-emergency, when would be an appropriate time to make that change in designation. (e.g. Annually, 90 days prior to desired change, etc.) A response by next Tuesday would be great, even if it involves a “We are working on that question and will include it in the FAQ that has an anticipated posting date of: month/day/year”. Billy Cutsor MEAN 402-474-4759 | To clarify, EPA Region 7 doesn't have any rule writers at all. All rules are written at Research Triangle Park in North Carolina. The rule writer for the RICE NESHAP is Melanie King, and she works there. Since it would be unreasonable for her to answer every rule question, there is EPA Regional delegation to answer questions on NESHAPs and NSPSs. When Nebraska adopts the rule into their state regulations, they'll be the administrator for the rule with EPA oversight. This question also came to me from Western Kansas and Lincoln. You'll want to clarify with your permitting agency, but technically you should have until the initial compliance date - May 3, 2013 - to designate whether your engine will be emergency or not. BUT, there are a few important things to note... 1) Even if the engines will be designated emergency, it would be a good idea to submit an initial notifications to EPA Region 7 and NDEQ. If they're non-emergency, they have to submit an initial notification (assuming your engine's at an area source for HAPs). 2) If the engine will be non-emergency, you'll have to be meeting the standard by May 3, 2013. That means you'll have to do a performance test to demonstrate compliance before that date and give NDEQ 60 days notice that you'll be doing the test. So, at the latest, realistically, you have until March 3, 2013 to designate as emergency/non-emergency.
2010-07-06 | Melissa Ellis | NESHAP 6X | Leslye Werner | Werner.Leslye@epamail.epa.gov (913) 551-7858 | Is EPA still implementing 6X for Metal Fab. such that applicability to the rule is based on the NAICS codes. I know we had this discussion a while back, but I'm checking on it again as I've had a question. As a reminder, the NAICS codes are not listed in the rule, but are only discussed in the preamble. It is my understanding that OECA is implementing the rule as it is written in the preamble. Can you confirm this? Thanks! | The last I heard, the rule applicability is based on the NAICS codes that are in the preamble. I haven't heard anything differently from DonnaLee Jones, the rule writer recently, so I assume that is still how we are handling this rule. Additionally, Len Lazarus has confirmed this position for OECA.
2010-06-22 | Melissa Ellis | NESHAP 4F | Joe (Hugh) McCullough | McCullough.Hugh@epamail.epa.gov | a source subject to 4F has group 2 continuous vent with TRE >5 & don't need control device to maintain the TRE value. They have a control device, does it need to meet monitoring requirements under Subpart SS? | No, since they don't use the device to comply with rule or maintain their TRE, they don't have to mointor according to Subpart SS.
2010-06-10 | Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | I have a question about 40 CFR part 63 Subpart ZZZZ. In 63.6612, it states a performance test doesn't have to be conducted if one has been conducted within 2 years. Is that 2 years from the rule promulgation, compliance date, or something else? | Under the general MACT provisions I thought deadlines like these were based off of the effective date of the rule, or 60 days after being posted in the federal register, but I can't find the right language to support that. In reading 63.6612, immediately following the "must not be older than 2 years" requirement, 63.6612 (b) (3) then says the test needs to be reviewed/accepted by the Administrator. So, I think you could make a healthy argument that if the test was reviewed and accepted by the administrator (in concordance with the new rule of course) in no more than 2 years before the promulgation date, then the source would have met its testing obligations. Not promulgation date - 2 years from effective date
2010-04-20 | Melissa Ellis | NESHAP 7D | Leslye Werner | Werner.Leslye@epamail.epa.gov (913) 551-7858 | Feed operations in NE utilizing manganese already have baghouses on the operations. The rule requires a cyclone and doesn't provide alternatives. Is a baghouse o.k.? Will the rule language change? Leslye checking with OAQPS & OECA.
2010-04-14 | Daive Graiver | NESHAP 4Z | Melanie King - OAQPS | Phone: (919) 541-2469 king.melanie@epa.gov | 63.6640(a) states that a facility must demonstrate compliance with limitations in Tables 2b and 2d using methods specified in table 6. Table 6 mentions nothing about complying with minimizing the engine's time spent at idle or minimizing the engine startup period. Should there be a monitoring and/or recordkeeping requirement for this or does EPA assume that monitoring/recordkeeping is not needed for this requirement? That is correct that there is no specific monitoring/recordkeeping requirement for the startup limit The operating limitation for item 2 of Table 2b states "Comply with any operating limitations approved by the Administrator." However there are no notification requirements for submitting operating limitations. How can a facility comply if nothing is ever sent or approved by the administrator? If a facility tests their engine and determines that the emission limitations are met through normal unaltered operation of the unit, would they need to send the administrator operating limitations (i.e. good combustion practices)? If the source wants to comply with operating limitations that are approved by the Administrator (i.e. something other than 1.a. and 1.b. in Table 2b) then they do need to submit those limitations to EPA and get them approved. Is the use of a CEMS or CPMS to comply with an emission limitation only allowed when presented as a compliance method in Table 5? For example, can an existing non emergency RICE >100 hp at an area source use a CEMS of CPMS to comply with its emission limitation? The rule doesn't really provide an option for existing diesel engines to use a CEMS, so I think they would need to get it approved, but I don't see why we wouldn't let someone do that. | From Rob Tobin: On the last point, I researched existing non emergency RICE <500 hp at an area source and found no CEMS option either, but from reading the other portions of the reg for other scenarios it was clear that such use was an escalation, a more protective route. Use of this would certainly be encouraged, but is not mandated. The idea that it would require prior approval seems contrary to the trend of the reg.
2010-04-05 | Melissa Ellis | NESHAP 6V | Leslye Werner | Werner.Leslye@epamail.epa.gov (913) 551-7858 | Can you give me the OECA contact for 6V? Randy McDonald indicated on the webinar that OECA believes ethanol plants are subject to the rule because the gasses are considered a by-product. Our permitting and compliance staff would like to hear that from them. The ATW says Marsha Mia is the contact, but her email came back to me as undeliverable. Thanks for your help! | As for 6V, I just emailed Randy and Marcia Mia. We have been discussing the 6V issue for Nebraska and other states. At this point they are fairly sure that the ethanol plants are subject, but we may have to do a formal applicability determination to get an official answer. I'm awaiting their reply to determine next steps. Pat Scott here has been communicating with your permitting group and we will get you all an answer as soon as we can. 4/13/10 Asked Leslye if they had heard anything yet. I was just telling Pat Scott for her NE permitting call today that Marcia Mia emailed me last week about the type of guidance we needed and I told her guidance on letterhead that we can share with the states. So far I haven't seen it, but I'm assuming she is working on it.
| Melissa Ellis | NESHAP 4Z | Eric Sturm | Sturm.Eric@epamail.epa.gov 913.551.7377 | Emergency engines and peaking - Questions from Tracy Henke Answers in Red are from Eric Sturm | We would like clarification on the following. Scenario #1: If a "hospital" uses their generator(s) for the purposes of 1) emergency standby power; and 2) use their generators to "peak shave" or for "curtailment" purposes, which would include a financial agreement to either: receive payment for running their generators to produce power connected tot he grid or reduce their current power bill, do they have to meet the current NESHAP requirements for a non-emergency engine? Example of hospitals in Omaha would be University of Nebraska Medical Center, Most of the Alegent Hospitals (Immanuel, Bergan Mercy, etc.). Any engine used for peak shaving will not be considered emergency under the rule. Peak shaving engines have to meet the requirements for non-emergency engines regardless of location. Scenario #2: A commercial customer (example: Qwest) uses their engines for the purposes of 1) emergency standby power; and 2) use their generators to "peak shave" or for "curtailment" purposes, which would include a financial agreement to either: receive payment for running their generators to produce power connected to the grid or reduce their current power bill, do they have to meet the current NESHAP requirements for a non-emergency engine? Again - Any engine used for peak shaving will not be considered emergency under the rule. Peak shaving engines have to meet the requirements for non-emergency engines regardless of location. Scenario #3: A municipality (City) uses their engines for the purposes of 1) emergency standby power; and 2) use their generators to "peak shave" or for "curtailment" purposes, which would include a financial agreement to either: receive payment for running their generators to produce power connected to the grid or reduce their current power bill, do they have to meet the current NESHAP requirements for a non-emergency engine? Is this an Institution? Again - Any engine used for peak shaving will not be considered emergency under the rule. Peak shaving engines have to meet the requirements for non-emergency engines regardless of location. Can you define institutional. Examples: Private hospitals versus hospitals that are funded by tax dollars, hospitals that include a college learning program. Are colleges institutions. Are their any institutions that are not hospitals or health cares, can you give examples? Attached -Guidance released with the recently amended SI RICE NESHAP standards, but only applicable to engines that are used for emergency purposes. NOT peaking.